## 1
Health Index Asset Category | Asset Register Category
LV OHL Support | LV Poles
LV UGB | LV UGB
LV Switchgear and Other | LV Board (WM)
LV Switchgear and Other | LV Board (X-type Network) (WM)
LV Switchgear and Other | LV Circuit Breaker
LV Switchgear and Other | LV Pillar (ID)
LV Switchgear and Other | LV Pillar (OD at Substation)
LV Switchgear and Other | LV Pillar (OD not at a Substation)
HV OHL Support - Poles | 6.6/11kV Poles
HV OHL Support - Poles | 20kV Poles
HV Switchgear (GM) - Primary | 6.6/11kV CB (GM) Primary
HV Switchgear (GM) - Primary | 20kV CB (GM) Primary
HV Switchgear (GM) - Distribution | 6.6/11kV CB (GM) Secondary
HV Switchgear (GM) - Distribution | 6.6/11kV RMU
HV Switchgear (GM) - Distribution | 6.6/11kV X-type RMU
HV Switchgear (GM) - Distribution | 6.6/11kV Switch (GM)
HV Switchgear (GM) - Distribution | 20kV CB (GM) Secondary
HV Switchgear (GM) - Distribution | 20kV RMU
HV Switchgear (GM) - Distribution | 20kV Switch (GM)
HV Transformer (GM) | 6.6/11kV Transformer (GM)
HV Transformer (GM) | 20kV Transformer (GM)
EHV OHL Support - Poles | 33kV Pole
EHV OHL Support - Poles | 66kV Pole
EHV OHL Fittings | 33kV Fittings
EHV OHL Fittings | 66kV Fittings
EHV OHL Conductor (Tower Lines) | 33kV OHL (Tower Line) Conductor
EHV OHL Conductor (Tower Lines) | 66kV OHL (Tower Line) Conductor
EHV OHL Support - Towers | 33kV Tower
EHV OHL Support - Towers | 66kV Tower
EHV UG Cable (Gas) | 33kV UG Cable (Gas)
EHV UG Cable (Gas) | 66kV UG Cable (Gas)
EHV UG Cable (Non Pressurised) | 33kV UG Cable (Non Pressurised)
EHV UG Cable (Non Pressurised) | 66kV UG Cable (Non Pressurised)
EHV UG Cable (Oil) | 33kV UG Cable (Oil)
EHV UG Cable (Oil) | 66kV UG Cable (Oil)
Submarine Cables | HV Sub Cable
Submarine Cables | EHV Sub Cable
Submarine Cables | 132kV Sub Cable
EHV Switchgear (GM) | 33kV CB (Air Insulated Busbars)(ID) (GM)
EHV Switchgear (GM) | 33kV CB (Air Insulated Busbars)(OD) (GM)
EHV Switchgear (GM) | 33kV CB (Gas Insulated Busbars)(ID) (GM)
EHV Switchgear (GM) | 33kV CB (Gas Insulated Busbars)(OD) (GM)
EHV Switchgear (GM) | 33kV RMU
EHV Switchgear (GM) | 33kV Switch (GM)
EHV Switchgear (GM) | 66kV CB (Air Insulated Busbars)(ID) (GM)
EHV Switchgear (GM) | 66kV CB (Air Insulated Busbars)(OD) (GM)
EHV Switchgear (GM) | 66kV CB (Gas Insulated Busbars)(ID) (GM)
EHV Switchgear (GM) | 66kV CB (Gas Insulated Busbars)(OD) (GM)
EHV Transformer | 33kV Transformer (GM)
EHV Transformer | 66kV Transformer (GM)
132kV OHL Fittings | 132kV Fittings
132kV OHL Conductor (Tower Lines) | 132kV OHL (Tower Line) Conductor
132kV OHL Support - Tower | 132kV Tower
132kV UG Cable (Gas) | 132kV UG Cable (Gas)
132kV UG Cable (Non Pressurised) | 132kV UG Cable (Non Pressurised)
132kV UG Cable (Oil) | 132kV UG Cable (Oil)
132kV CBs | 132kV CB (Air Insulated Busbars)(ID) (GM)
132kV CBs | 132kV CB (Air Insulated Busbars)(OD) (GM)
132kV CBs | 132kV CB (Gas Insulated Busbars)(ID) (GM)
132kV CBs | 132kV CB (Gas Insulated Busbars)(OD) (GM)
132kV Transformer | 132kV Transformer (GM)

## 2
Generic Term | Generic Term | Health Index Asset Category
Cable | Pressurised Cable | EHV UG Cable (Oil)
Cable | Pressurised Cable | EHV UG Cable (Gas)
Cable | Pressurised Cable | 132kV UG Cable (Oil)
Cable | Pressurised Cable | 132kV UG Cable (Gas)
Cable | Non Pressurised Cable | EHV UG Cable (Non Pressurised)
Cable | Non Pressurised Cable | 132kV UG Cable (Non Pressurised)
Cable | Non Pressurised Cable | Submarine Cables
Switchgear |  | LV Switchgear and Other
Switchgear |  | LV UGB
Switchgear |  | HV Switchgear (GM) - Distribution
Switchgear |  | HV Switchgear (GM) - Primary
Switchgear |  | EHV Switchgear (GM)
Switchgear |  | 132kV CBs
Transformers | HV Transformer | HV Transformer (GM)
Transformers | Grid & Primary (or EHV & 132kV) Transformers | EHV Transformer
Transformers | Grid & Primary (or EHV & 132kV) Transformers | 132kV Transformer
Overhead Line | Poles | LV OHL Support
Overhead Line | Poles | EHV OHL Support - Poles
Overhead Line | Poles | HV OHL Support - Poles
Overhead Line | Towers | EHV OHL Support - Towers
Overhead Line | Towers | 132kV OHL Support - Towers
Overhead Line | Fittings | EHV OHL Fittings
Overhead Line | Fittings | 132kV OHL Fittings
Overhead Line | OHL Conductor | EHV OHL Conductor (Tower Lines)
Overhead Line | OHL Conductor | 132kV OHL Conductor (Tower Lines)

## 3
Asset Register Category | Voltage
LV Main (OHL) Conductor | LV
LV Service (OHL) | LV
LV Main (UG Consac) | LV
LV Main (UG Plastic) | LV
LV Main (UG Paper) | LV
Rising & Lateral Mains | LV
LV Service (UG) | LV
LV Service associated with RLM | LV
Cut Out (Metered) | LV
LV Transformers/Regulators | LV
6.6/11kV OHL (Conventional Conductor) | HV
6.6/11kV OHL (BLX or similar Conductor) | HV
20kV OHL (Conventional Conductor) | HV
20kV OHL (BLX or similar Conductor) | HV
6.6/11kV UG Cable | HV
20kV UG Cable | HV
6.6/11kV CB (PM) | HV
6.6/11kV Switch (PM) | HV
6.6/11kV Switchgear - Other (PM) | HV
20kV CB (PM) | HV
20kV Switch (PM) | HV
20kV Switchgear - Other (PM) | HV
6.6/11kV Transformer (PM) | HV
20kV Transformer (PM) | HV
Batteries at GM HV Substations | HV
33kV OHL (Pole Line) Conductor | EHV
66kV OHL (Pole Line) Conductor | EHV
33kV Switchgear - Other | EHV
33kV Switch (PM) | EHV
66kV Switchgear - Other | EHV
33kV Transformer (PM) | EHV
Batteries at 33kV Substations | EHV
Batteries at 66kV Substations | EHV
132kV OHL (Pole Line) Conductor | 132kV
132kV Pole | 132kV
132kV Switchgear - Other | 132kV
Batteries at 132kV Substations | 132kV
Pilot Wire Overhead | Other
Pilot Wire Underground | Other
Cable Tunnel (DNO owned) | Other
Cable Bridge (DNO owned) | Other
Electrical Energy Storage | Other

## 4
Functional Failure Type | Description
Catastrophic | A sudden and total failure from which recovery of the asset (and or sub component) is not feasible.
Degraded | A significant failure associated with advanced degradation.
Incipient | A minor failure associated with early stage degradation

## 5
Health Index Band | Lower | Upper | Bound Description
HI1 | 0.5 | 4 | Limit of Health Score
HI2 | 4 | 5.5 | Limit of Health Score
HI3 | 5.5 | 6.5 | Limit of Health Score
HI4 | 6.5 | 8 | Limit of Health Score
HI5 | 8 | 15 | Limit of Health Score

## 6
Health Index Band | Health Score to be used to derive Average PoF
HI1 | 4
HI2 | 4.75
HI3 | 6
HI4 | 7.25
HI5 | 10

## 7
Criticality Index Band | Lower | Upper | Bound Description | Value to be used to calculate Risk Index (stipulated in the NAW) in %
C1 | 0 | 75 | Overall CoF (as % of Average Overall CoF for the Asset Category) | 70
C2 | 75 | 125 | Overall CoF (as % of Average Overall CoF for the Asset Category) | 100
C3 | 125 | 200 | Overall CoF (as % of Average Overall CoF for the Asset Category) | 150
C4 | 200 |  | Overall CoF (as % of Average Overall CoF for the Asset Category) | 250

## 8
Asset Category | Duty Factor 1 (DF1) | Duty Factor 2 (DF2)
Cables | % Utilisation | Operating Voltage ÷ Design Voltage
Poles | No asset-specific Duty Factor 1 (i.e. DF1 = 1) | N/A
LV UGB | No asset-specific Duty Factor 1 (i.e. DF1 = 1) | N/A
Switchgear - LV | No asset-specific Duty Factor 1 (i.e. DF1 = 1) | N/A
Switchgear - HV Distribution | No asset-specific Duty Factor 1 (i.e. DF1 = 1) | N/A
Switchgear - HV Primary | Number of Operations | N/A
Switchgear - EHV & 132kV | Number of Operations | N/A
Steel Tower | No asset-specific Duty Factor 1 (i.e. DF1 = 1) | N/A
Conductor | No asset-specific Duty Factor 1 (i.e. DF1 = 1) | N/A
Fittings | No asset-specific Duty Factor 1 (i.e. DF1 = 1) | N/A
HV Transformer (GM) | % Utilisation | N/A
HV Transformer (GM) | Transformer: % Utilisation | N/A
Transformers - EHV & 132kV | Tapchanger: Average Number of Daily Tapping Operations | N/A

## 9
a = Maximum of (Observed Condition Factor, Measured Condition Factor) | b = Minimum of (Observed Condition Factor, Measured Condition Factor) | Health Score Factor
>1 | >1 | = a + ((b-1)/1.5)
>1 | ≤1 | = a
≤1 | ≤1 | = b + ((a-1)/1.5)

## 10
Parameters for Combination Using MMI Technique - Factor Divider 1 | Parameters for Combination Using MMI Technique - Factor Divider 2 | Parameters for Combination Using MMI Technique - Max. No. of Condition Factors
1.5 | 1.5 | 4

## 11
Parameters for Combination Using MMI Technique - Factor Divider 1 | Parameters for Combination Using MMI Technique - Factor Divider 2 | Parameters for Combination Using MMI Technique - Max. No. of Condition Factors
1.5 | 1.5 | 2

## 12
Asset Category | Subcomponent | Observed Condition Input
LV UGB | N/A | 1. Steel Cover and Pit condition, 2. Water/Moisture, 3. Bell Condition, 4. Insulation Condition, 5. Signs of heating, 6. Phase Barriers
LV Circuit Breaker | N/A | 1. Switchgear external condition
LV Board (WM) | N/A | 1. Switchgear external condition, 2. Compound Leaks, 3. Switchgear internal condition
LV Pillars | N/A | 1. Switchgear external condition, 2. Compound Leaks, 3. Switchgear internal condition, 4. Insulation, 5. Signs of Heating, 6. Phase Barriers
HV Switchgear (GM) - Primary | N/A | 1. Switchgear external condition, 2. Oil leaks/ Gas pressure, 3. Thermographic Assessment, 4. Switchgear internal condition and operation, 5. Indoor Environment
HV Switchgear (GM) - Distribution | N/A | 1. Switchgear external condition, 2. Oil leaks/ Gas pressure, 3. Thermographic Assessment, 4. Switchgear internal condition and operation, 5. Indoor Environment
EHV Switchgear (GM) | N/A | 1. Switchgear external condition, 2. Oil leaks/ Gas pressure, 3. Thermographic Assessment, 4. Switchgear internal condition and operation, 5. Indoor Environment, 6. Support Structures
132kV Switchgear (GM) | N/A | 1. Switchgear external condition 2. Oil leaks/ Gas pressure 3. Thermographic Assessment 4. Switchgear internal condition and operation 5. Indoor Environment, 6. Support Structures 7. Air systems
HV Transformer (GM) | N/A | 1. Transformer external condition
EHV Transformer (GM) | Main Transformer | 1. Main tank condition, 2. Coolers/Radiator condition 3. Bushings condition 4. Kiosk condition 5. Cable boxes condition
EHV Transformer (GM) | Tapchanger | 1. Tapchanger external condition, 2. Internal Condition, 3. Drive Mechanism Condition, 4. Condition of Selector & Diverter Contacts, 5. Condition of Selector & Diverter Braids
132kV Transformer (GM) | Main Transformer | 1. Main tank condition, 2. Coolers/Radiator condition 3. Bushings condition 4. Kiosk condition 5. Cable boxes condition
132kV Transformer (GM) | Tapchanger | 1. Tapchanger external condition, 2. Internal Condition, 3. Drive Mechanism Condition, 4. Condition of Selector & Diverter Contacts, 5. Condition of Selector & Diverter Braids
EHV Cable (Non Pressurised) | N/A | None
EHV Cable (Oil) | N/A | None
EHV Cable (Gas) | N/A | None
132kV Cable (Non Pressurised) | N/A | None
132kV Cable (Oil) | N/A | None
132kV Cable (Gas) | N/A | None
Submarine Cable | N/A | 1. External Condition of Armour
LV Poles | N/A | 1. Visual Pole Condition, 2. Pole Top Rot, 3. Pole Leaning, 4. Bird / Animal Damage
HV Poles | N/A | 1. Visual Pole Condition, 2. Pole Top Rot, 3. Pole Leaning, 4. Bird / Animal Damage
EHV Poles | N/A | 1. Visual Pole Condition, 2. Pole Top Rot, 3. Pole Leaning, 4. Bird / Animal Damage
EHV Towers | Tower Steelwork | 1. Tower Legs, 2. Bracings, 3. Crossarms, 4. Peak
EHV Towers | Tower Paintwork | 1. Paintwork Condition
EHV Towers | Foundations | 1. Foundation Condition
132kV Towers | Tower Steelwork | 1. Tower Legs, 2. Bracings, 3. Crossarms, 4. Peak
132kV Towers | Tower Paintwork | 1. Paintwork Condition
132kV Towers | Foundations | 1. Foundation Condition
EHV Fittings | N/A | 1. Tower fittings, 2. Conductor fittings, 3. Insulators - Electrical, 4. Insulators - Mechanical
132kV Fittings | N/A | 1. Tower fittings, 2. Conductor fittings, 3. Insulators - Electrical, 4. Insulators - Mechanical
EHV Tower Line Conductor | N/A | 1. Visual Condition, 2. Midspan joints
132kV Tower Line Conductor | N/A | 1. Visual Condition, 2. Midspan joints

## 13
Asset Category | Subcomponent | Parameters for Combination Using MMI Technique - Factor Divider 1 | Parameters for Combination Using MMI Technique - Factor Divider 2 | Parameters for Combination Using MMI Technique - Max. No. of Combined Factors
LV UGB | N/A | 1.5 | 1.5 | 3
LV Circuit Breaker | N/A | 1.5 | 1.5 | 1
LV Board (WM) | N/A | 1.5 | 1.5 | 2
LV Pillars | N/A | 1.5 | 1.5 | 3
HV Switchgear (GM) - Primary | N/A | 1.5 | 1.5 | 3
HV Switchgear (GM) - Distribution | N/A | 1.5 | 1.5 | 3
EHV Switchgear (GM) | N/A | 1.5 | 1.5 | 3
132kV Switchgear (GM) | N/A | 1.5 | 1.5 | 3
HV Transformer (GM) | N/A | 1.5 | 1.5 | 1
EHV Transformer (GM) | Main Transformer | 1.5 | 1.5 | 3
EHV Transformer (GM) | Tapchanger | 1.5 | 1.5 | 3
132kV Transformer (GM) | Main Transformer | 1.5 | 1.5 | 3
132kV Transformer (GM) | Tapchanger | 1.5 | 1.5 | 3
Submarine Cable | N/A | 1.5 | 1.5 | 1
LV Poles | N/A | 1.5 | 1.5 | 2
HV Poles | N/A | 1.5 | 1.5 | 2
EHV Poles | N/A | 1.5 | 1.5 | 2
EHV Towers | Tower Steelwork | 1.5 | 1.5 | 3
EHV Towers | Tower Paintwork | 1.5 | 1.5 | 1
EHV Towers | Foundations | 1.5 | 1.5 | 1
132kV Towers | Tower Steelwork | 1.5 | 1.5 | 3
132kV Towers | Tower Paintwork | 1.5 | 1.5 | 1
132kV Towers | Foundations | 1.5 | 1.5 | 1
EHV Fittings | N/A | 1.5 | 1.5 | 3
132kV Fittings | N/A | 1.5 | 1.5 | 3
EHV Tower Line Conductor | N/A | 1.5 | 1.5 | 1
132kV Tower Line Conductor | N/A | 1.5 | 1.5 | 1
EHV Cable (Non Pressurised) | N/A | N/A | N/A | N/A
EHV Cable (Oil) | N/A | N/A | N/A | N/A
EHV Cable (Gas) | N/A | N/A | N/A | N/A
132kV Cable (Non Pressurised) | N/A | N/A | N/A | N/A
132kV Cable (Oil) | N/A | N/A | N/A | N/A
132kV Cable (Gas) | N/A | N/A | N/A | N/A

## 14
Asset Category | Subcomponent | Measured Condition Input
LV UGB | N/A | 1. Operational Adequacy
LV Circuit Breaker | N/A | 1. Operational Adequacy
LV Board (WM) | N/A | 1. Operational Adequacy, 2. Security
LV Pillars | N/A | 1. Operational Adequacy
HV Switchgear (GM) - Primary | N/A | 1. Partial Discharge, 2. Ductor Test, 3. IR Test, 4. Oil Tests, 5. Temperature Readings, 6. Trip Test
HV Switchgear (GM) - Distribution | N/A | 1. Partial Discharge, 2. Ductor Test, 3. Oil Tests, 4. Temperature Readings, 5. Trip Test
EHV Switchgear (GM) | N/A | 1. Partial Discharge, 2. Ductor Test, 3. IR Test, 4. Oil Tests/ Gas Tests, 5. Temperature Readings, 6. Trip Test
132kV Switchgear (GM) | N/A | 1. Partial Discharge, 2. Ductor Test, 3. IR Test, 4. Oil Tests/ Gas Tests, 5. Temperature Readings, 6. Trip Test
HV Transformer (GM) | N/A | 1. Partial Discharge, 2. Oil Acidity, 3. Temperature Readings
EHV Transformer (GM) | Main Transformer | 1. Partial Discharge, 2. Temperature Readings
EHV Transformer (GM) | Tapchanger | 1. Tapchanger Partial Discharge
132kV Transformer | Main Transformer | 1. Partial Discharge 2. Temperature Readings
132kV Transformer | Tapchanger | 1. Tapchanger Partial Discharge
EHV Cable (Non Pressurised) | N/A | 1. Sheath Test, 2. Partial Discharge, 3. Fault history
EHV Cable (Oil) | N/A | 1. Leakage
EHV Cable (Gas) | N/A | 1. Leakage
132kV Cable (Non Pressurised) | N/A | 1. Sheath Test, 2. Partial Discharge, 3. Fault history
132kV Cable (Oil) | N/A | 1. Leakage
132kV Cable (Gas) | N/A | 1. Leakage
Submarine Cable | N/A | 1. Sheath Test, 2. Partial Discharge, 3. Fault history
LV Poles | N/A | 1. Pole decay / deterioration
HV Poles | N/A | 1. Pole decay / deterioration
EHV Poles | N/A | 1. Pole decay / deterioration
EHV Towers | Tower Steelwork | None
EHV Towers | Tower Paintwork | None
EHV Towers | Foundations | None
132kV Towers | Tower Steelwork | None
132kV Towers | Tower Paintwork | None
132kV Towers | Foundations | None
EHV Fittings | N/A | 1. Thermal Imaging, 2. Ductor Tests
132kV Fittings | N/A | 1. Thermal Imaging, 2. Ductor Tests
EHV Tower Line Conductor | N/A | 1. Conductor Sampling, 2. Corrosion Monitoring Survey
132kV Tower Line Conductor | N/A | 1. Conductor Sampling, 2. Corrosion Monitoring Survey

## 15
Asset Category | Subcomponent | Parameters for Combination Using MMI Technique - Factor Divider 1 | Parameters for Combination Using MMI Technique - Factor Divider 2 | Parameters for Combination Using MMI Technique - Max. No. of Combined Factors
LV UGB | N/A | 1.5 | 1.5 | 1
LV Circuit Breaker | N/A | 1.5 | 1.5 | 1
LV Board (WM) | N/A | 1.5 | 1.5 | 2
LV Pillars | N/A | 1.5 | 1.5 | 1
HV Switchgear (GM) - Primary | N/A | 1.5 | 1.5 | 3
HV Switchgear (GM) - Distribution | N/A | 1.5 | 1.5 | 3
EHV Switchgear (GM) | N/A | 1.5 | 1.5 | 3
132kV Switchgear (GM) | N/A | 1.5 | 1.5 | 3
HV Transformer (GM) | N/A | 1.5 | 1.5 | 2
EHV Transformer (GM) | Main Transformer | 1.5 | 1.5 | 2
EHV Transformer (GM) | Tapchanger | 1.5 | 1.5 | 1
132kV Transformer (GM) | Main Transformer | 1.5 | 1.5 | 2
132kV Transformer (GM) | Tapchanger | 1.5 | 1.5 | 1
EHV Cable (Non Pressurised) | N/A | 1.5 | 1.5 | 2
EHV Cable (Oil) | N/A | 1.5 | 1.5 | 1
EHV Cable (Gas) | N/A | 1.5 | 1.5 | 1
132kV Cable (Non Pressurised) | N/A | 1.5 | 1.5 | 2
132kV Cable (Oil) | N/A | 1.5 | 1.5 | 1
132kV Cable (Gas) | N/A | 1.5 | 1.5 | 1
Submarine Cable | N/A | 1.5 | 1.5 | 2
LV Poles | N/A | 1.5 | 1.5 | 1
HV Poles | N/A | 1.5 | 1.5 | 1
EHV Poles | N/A | 1.5 | 1.5 | 1
EHV Fittings | N/A | 1.5 | 1.5 | 1
132kV Fittings | N/A | 1.5 | 1.5 | 1
EHV Tower Line Conductor | N/A | 1.5 | 1.5 | 1
132kV Tower Line Conductor | N/A | 1.5 | 1.5 | 1
EHV Towers | Tower Steelwork | N/A | N/A | N/A
EHV Towers | Tower Paintwork | N/A | N/A | N/A
EHV Towers | Foundations | N/A | N/A | N/A
132kV Towers | Tower Steelwork | N/A | N/A | N/A
132kV Towers | Tower Paintwork | N/A | N/A | N/A
132kV Towers | Foundations | N/A | N/A | N/A

## 16
Asset Register Category | Financial - (GBP) | Safety - (GBP) | Environmental - (GBP) | Network Performance - (GBP) | Total - (GBP)
LV Poles | 1113 | 536 | 75 | 1218 | 2942
6.6/11kV Poles | 1592 | 179 | 75 | 1297 | 3143
20kV Poles | 1910 | 179 | 75 | 1297 | 3461
33kV Pole | 2053 | 179 | 75 | 57 | 2364
66kV Pole | 3094 | 179 | 75 | 114 | 3462
33kV Tower | 5618 | 334 | 155 | 362 | 6469
66kV Tower | 10527 | 334 | 155 | 1039 | 12055
132kV Tower | 12172 | 334 | 155 | 2077 | 14738
33kV Fittings | 189 | 1336 | 80 | 167 | 1772
66kV Fittings | 243 | 1336 | 80 | 333 | 1992
132kV Fittings | 404 | 1336 | 80 | 666 | 2486
33kV OHL (Tower Line) Conductor | 14811 | 1336 | 80 | 833 | 17060
66kV OHL (Tower Line) Conductor | 19644 | 1336 | 80 | 1666 | 22726
132kV OHL (Tower Line) Conductor | 16988 | 1336 | 80 | 3331 | 21735
HV Sub Cable | 151492 | 2 | 3000 | 160627 | 315121
33kV UG Cable (Non Pressurised) | 26340 | 2 | 605 | 2572 | 29519
33kV UG Cable (Oil) | 108 | 2 | 4898 | 3 | 5011
33kV UG Cable (Gas) | 264 | 2 | 45 | 26 | 337
66kV UG Cable (Non Pressurised) | 53291 | 2 | 605 | 5144 | 59042
66kV UG Cable (Oil) | 116 | 2 | 4898 | 5 | 5021
66kV UG Cable (Gas) | 432 | 2 | 45 | 51 | 530
132kV UG Cable (Non Pressurised) | 90934 | 2 | 905 | 10287 | 102128
132kV UG Cable (Oil) | 129 | 2 | 6167 | 10 | 6308
132kV UG Cable (Gas) | 667 | 2 | 67 | 103 | 839
EHV Sub Cable | 237500 | 2 | 3000 | 2572 | 243074
132kV Sub Cable | 400000 | 2 | 3000 | 10287 | 413289
LV Circuit Breaker | 3388 | 8050 | 18 | 12436 | 23892
LV Pillar (ID) | 4719 | 8050 | 18 | 9247 | 22034
LV Pillar (OD at Substation) | 5136 | 8050 | 18 | 9247 | 22451
LV Pillar (OD not at a Substation) | 2854 | 8504 | 18 | 9247 | 20623
LV UGB | 2854 | 8504 | 71 | 3699 | 15128
LV Board (WM) | 6520 | 8050 | 18 | 9247 | 23835
LV Board (X-type Network) (WM) | 7694 | 8050 | 18 | 9247 | 25009
6.6/11kV CB (GM) Primary | 6315 | 20771 | 1141 | 9725 | 37952
6.6/11kV CB (GM) Secondary | 5792 | 4262 | 1108 | 7780 | 18942
6.6/11kV Switch (GM) | 4384 | 4262 | 1108 | 7780 | 17534
6.6/11kV RMU | 8190 | 4262 | 1108 | 7780 | 21340
6.6/11kV X-type RMU | 11083 | 4262 | 1108 | 7780 | 24233
20kV CB (GM) Primary | 7911 | 20771 | 1141 | 9725 | 39548
20kV CB (GM) Secondary | 6005 | 4262 | 1108 | 7780 | 19155
20kV Switch (GM) | 5081 | 4262 | 1108 | 7780 | 18231
20kV RMU | 8343 | 4262 | 1108 | 7780 | 21493
33kV CB (Air Insulated Busbars)(ID) (GM) | 12081 | 20771 | 2589 | 24248 | 59689
33kV CB (Air Insulated Busbars)(OD) (GM) | 14874 | 20771 | 2589 | 12274 | 50508
33kV CB (Gas Insulated Busbars)(ID) (GM) | 18299 | 20771 | 2589 | 24248 | 65907
33kV CB (Gas Insulated Busbars)(OD) (GM) | 18299 | 20771 | 2589 | 12274 | 53933
33kV Switch (GM) | 8537 | 20771 | 2589 | 12274 | 44171
33kV RMU | 21099 | 20771 | 2589 | 12274 | 56733
66kV CB (Air Insulated Busbars)(ID) (GM) | 24081 | 20771 | 2589 | 24248 | 71689
66kV CB (Air Insulated Busbars)(OD) (GM) | 38500 | 20771 | 2589 | 12274 | 74134
66kV CB (Gas Insulated Busbars)(ID) (GM) | 43431 | 20771 | 2589 | 24248 | 91039
66kV CB (Gas Insulated Busbars)(OD) (GM) | 43431 | 20771 | 2589 | 12274 | 79065
132kV CB (Air Insulated Busbars)(ID) (GM) | 67501 | 31968 | 7102 | 128126 | 234697
132kV CB (Air Insulated Busbars)(OD) (GM) | 31781 | 31968 | 7102 | 32331 | 103182
132kV CB (Gas Insulated Busbars)(ID) (GM) | 140585 | 31968 | 7102 | 128126 | 307781
132kV CB (Gas Insulated Busbars)(OD) (GM) | 140585 | 31968 | 7102 | 32331 | 211986
6.6/11kV Transformer (GM) | 7739 | 4262 | 3171 | 4862 | 20034
20kV Transformer (GM) | 8811 | 4262 | 3171 | 4862 | 21106
33kV Transformer (GM) | 73000 | 20771 | 14190 | 48197 | 156158
66kV Transformer (GM) | 112203 | 20771 | 14190 | 48197 | 195361
132kV Transformer (GM) | 218932 | 31968 | 29212 | 255853 | 535965

## 17
Fixed value | Source
Environmental cost per litre oil (GBP/litre) | This is derived from the EU trading value for carbon emissions and is consistent with the value used in Ofgem's RIIO-ED1 Cost Benefit Analysis template (used for the RIIO-ED1 submissions) (at 2012/13 prices)
Traded carbon price (GBP/t) | https://www.gov.uk/carbon-valuation (note: 2016 to 2030 DECC's updated traded sector carbon values published Oct 2012, 2031 onwards based on DECC carbon values published Oct 2011.) ; http://www.defra.gov.uk/publications/2012/05/30/pb13773-2012-ghg-conversion/ (note: figures taken from 2012 Guideline to Defra / DECC's GHG conversion factors for company reporting, 'new 2010' factor annex 3 table 3(c).
Conversion factor for cost of SF6 loss c/w cost of carbon (kg CO2e/kg) | 2011/12 Defra conversion factor (at 2012/13 prices)

## 18
Lower | Upper | Bound Description | No. of Customers to be used in the derivation of Customer Factor
0 | 50 | Maximum Demand on Asset / Total Number of Customers fed by the Asset (kVA per Customer) | 1 x actual number of customers fed by the asset
50 | 100 | Maximum Demand on Asset / Total Number of Customers fed by the Asset (kVA per Customer) | 25 x actual number of customers fed by the asset
100 | 500 | Maximum Demand on Asset / Total Number of Customers fed by the Asset (kVA per Customer) | 100 x actual number of customers fed by the asset
500 | 1000 | Maximum Demand on Asset / Total Number of Customers fed by the Asset (kVA per Customer) | 250 x actual number of customers fed by the asset
1000 | 2000 | Maximum Demand on Asset / Total Number of Customers fed by the Asset (kVA per Customer) | 500 x actual number of customers fed by the asset
2000 |  | Maximum Demand on Asset / Total Number of Customers fed by the Asset (kVA per Customer) | 1000 x actual number of customers fed by the asset

## 19
Asset Category | Function | Failure modes | Catastrophic Failure | Degraded Failures | Incipient Failures | Functional failures excluded
LV Circuit Breaker | Measure and break unsafe levels of current (over current), make load current, and provide a point of electrical isolation. | Failing to open on a fault. Failing to close reliably. Failing to open during manual operation. Failure to supply load current (i.e. failure during normal operating conditions). Opens Spuriously under normal conditions. Opens Intermittently (Faulty). | Failure of Housing. Disruptive Failure Resulting from Insulation Breakdown. | Nuisance tripping or failure to operate when required due to: 1. damage to contacts 2. loose internal connections 3. Damage to mechanism and drive rods. | Nuisance tripping or failure to operate when required due to: - Maladjusted linkage. | Failure of protection module., Failure of SCADA.
LV Pillar (ID) | Provide a number of points of access to LV Cable Systems for electrical connection, isolation and flexibility with network reconfiguration. Depending on the complexity of pillar they may also offer monitoring and protection (fuse or circuit breaker) capabilities. | Failing to close reliably. Failing to open during manual operation. Failure to supply load current (i.e. failure during normal operating conditions). | Failure of Housing. Disruptive Failure Resulting from Insulation Breakdown requiring the replacement of one or all ways. | Failure of Housing requiring repair. Nuisance tripping or Failure of an LV Pillar's Fuse, MCB or RCBO to operate when required due to: 1. deteriorated fuse carriers 2. breaker stuck closed. | Nuisance tripping or Failure of an LV Pillar's Fuse, MCB or RCBO to operate when required due to: 1. incorrect fuse/breaker rating 2. breaker not latching closed. | Contact damage due to incorrect operation of board.
LV Pillar (OD at Substation / LV Pillar (OD not at a Substation) | Provide a number of points of access to LV Cable Systems for electrical connection, isolation and flexibility with network reconfiguration. Depending on the complexity of pillar they may also offer monitoring and protection (fuse or circuit breaker) capabilities. | Failing to close reliably. Failing to open during manual operation. Failure to supply load current (i.e. failure during normal operating conditions). | Failure of Housing. Disruptive Failure Resulting from Insulation Breakdown requiring the replacement of one or all ways. | Failure of Housing requiring repair. Nuisance tripping or Failure of an LV Pillar's Fuse, MCB or RCBO to operate when required due to: 1. deteriorated fuse carriers 2. breaker stuck closed. | Nuisance tripping or Failure of an LV Pillar's Fuse, MCB or RCBO to operate when required due to: 1. incorrect fuse/breaker rating 2. breaker not latching closed. | Contact damage due to incorrect operation of board.
LV Board (WM) | Provide a number of points of access to LV Cable Systems for electrical connection, isolation and flexibility with network reconfiguration. Depending on the complexity of LV Board, they may also offer monitoring and protection (fuse or circuit breaker) capabilities. | Failing to open on a fault. Failing to close reliably. Failing to open during manual operation. Failure to supply load current (i.e. failure during normal operating conditions). Opens Spuriously under normal conditions. Opens Intermittently (Faulty). | Disruptive Failure Resulting from Insulation Breakdown. | Nuisance tripping or failure to operate when required due to: 1. damage to contacts, 2. moisture ingress, 3. deteriorated fuse carriers. | Nuisance tripping or failure to operate when required due to: 1. damage to contacts, 2. loose internal connections, 3. failure of protection module. | Failure of housing. Contact Damage due to Incorrect operation of Board.
LV UGB | Provide a number of points of access to LV Cable Systems for electrical connection, isolation and flexibility with network reconfiguration. Depending on the complexity of the LV Box, they may also offer monitoring and protection (fuse or circuit breaker) capabilities. | Failing to open on a fault (if used in this mode. Failing to close reliably. Failing to open during manual operation. Failure to supply load current (i.e. failure during normal operating conditions). Opens Spuriously under normal conditions. Opens Intermittently (Faulty). | Disruptive Failure Resulting from Insulation Breakdown. | Failure to be operable when required due to: 1. damage to contacts, 2. moisture ingress, 3. deteriorated links. | Failure to be operable when required due to: 1. damage to contacts, 2. loose internal connections. | Failure of housing. Contact Damage due to Incorrect operation of Box.
HV Switchgear (GM) – Primary / HV Switchgear (GM) - Distribution | Carry, make or break continuous load or fault current. Maintain or interrupt voltage on all three phases. Isolation & Earthing of Cables & Plant. Measurement of current and voltage. | Does not open or close on command (Where this is associated with the Breaker and not the control system). , Mechanical Failure. , Electrical Failure (Auxiliary & Control). , Electrical Failure (Main Circuit). | Disruptive Failure Resulting from Insulation Breakdown. | SOP preventing operation. Failure to operate when required due to: 1. Failure of Mechanism, 2. Protection module, 3. CT Failure, 4. VT Failure, 5.Stuck Breaker. | Failure to operate when required due to: - Low Gas Lockout or Vacuum bottle condition. | Unable to withstand impulse voltage. Unable to contain the insulating medium. Does not allow switch tank to breath. Unable to support its own weight. Does not provide a connection to the substation earth mat.
EHV Switchgear (GM) | Carry, make or break continuous load or fault current. Maintain or interrupt voltage on all three phases. Isolation & Earthing of Cables & Plant. Measurement of current and voltage. | Does not open or close on command (Where this is associated with the Breaker and not the control system). Mechanical Failure. Electrical Failure (Auxiliary & Control). Electrical Failure (Main Circuit). | Disruptive Failure Resulting from Insulation Breakdown. | SOP preventing operation. Failure to operate when required due to: 1. Failure of Mechanism, 2. Protection module, 3. CT Failure, 4. VT Failure, 5. Stuck Breaker. | Failure to operate when required due to: - Low Gas Lockout or Vacuum bottle condition. | Unable to withstand impulse voltage. Unable to contain the insulating medium. Does not allow switch tank to breath. Unable to support its own weight. Does not provide a connection to the substation earth mat. Failure of civil structures or associated disconnectors. Any asset classed by RIG definition as EHV Swgr Other.
132kV CBs | Carry, make or break continuous load or fault current. Maintain or interrupt voltage on all three phases. Isolation & Earthing of Cables & Plant. Measurement of current and voltage. | Does not open or close on command (Where this is associated with the Breaker and not the control system). Mechanical Failure. Electrical Failure (Auxiliary & Control). Electrical Failure (Main Circuit). | Disruptive Failure Resulting from Insulation Breakdown. | SOP preventing operation. Failure to operate when required due to: 1. Failure of Mechanism, 2. Protection module, 3. CT Failure, 4. VT Failure, 5. Stuck Breaker. | Failure to operate when required due to: - Low Gas Lockout or Vacuum bottle condition. | Unable to withstand impulse voltage. Unable to contain the insulating medium. Does not allow switch tank to breath. Unable to support its own weight. Does not provide a connection to the substation earth mat. Failure of civil structures or associated disconnectors. Any asset classed by RIG definition as EHV Swgr Other.
HV Transformer (GM) | Step up or step down and provide a secondary output voltage which is within statutory limits. Carry full load current when required. Carry through fault current when required. | Tapchanger, bushing, windings, core, tank or insulation failure. | Failure of the main internal components - windings, core or insulation. | Failure of the bushing, cable termination, including box and conservator tank. | Failure of the Tapchanger. | Oil condition corrected by an oil change and not re-conditioning, levels and leaks. Cable connection to controlling switchgear. Civil structure related failures
EHV Transformer / 132kV Transformer | Step up or step down and provide a secondary output voltage which is within statutory limits. Carry full load current when required. Carry through fault current when required. | Tapchanger, bushing, windings, core, tank, insulation or control/monitoring failure. | Failure of the tank or main internal components - windings, core or insulation. | Failure of the bushing, cable termination conservator tank and associated radiator. | Failure of the Tapchanger. | Oil condition corrected by an oil change and not re-conditioning, levels and leaks. CT's, VT's and on tank unit auxiliary transformers associated with the unit NER's and NEX's Neutral displacement VT's. Cable and busbar connection to controlling switchgear. Civil structure related failures. Buchholz.
Poles | Support electrical equipment in compliance with the ESQCR and Construction Regulations. | Decayed Pole. Decayed Struts. Snapped Stays. | Any structure whose components have either failed (broken) or whose residual strength has decreased to a level where immediate replacement of all or part of the structure is required. | Any structure whose components have a residual strength such that replacement is required within the timescale defined by the Company. | Vermin Damage resulting in Factor of Safety reduction requiring an intervention. | Broken Conductor. Broken or damaged fittings. Damaged or non-functioning plant. Broken or damaged insulation. Missing or degraded safety signs and anti climbing fixtures. Leaning poles where statutory clearances are not impacted. Cable boxes and platforms, including sealing ends.
Towers | Support electrical equipment in compliance with the ESQCR. | Corrosion or distortion of the structure, i.e. bent member, failing foundations. | Any structure whose components have either failed (broken) or whose residual strength has decreased to a level where immediate replacement of all or part of the structure is required. | Any component of the structure who's condition is such that it prevents normal operation of the Tower, or degrades the residual strength of the Tower, requiring an intervention with in a defined period. | Corrosion to minor Tower components and land movements degrading the potential of the Towers stability. | Broken Conductor. Broken or damaged fittings. Broken or damaged insulation. Missing or degraded safety signs and anti-climbing fixtures. Cable boxes and platforms, including sealing ends.
Fittings / OHL Conductor | Carry load and fault current without annealing or sagging below the ESQCR limit. Maintain continuity under normal and fault conditions. Provide phase-phase and phase-earth insulation. | Flashover. Insulation failure. Corroded Conductor. Corroded Jumper. Corroded Fitting. | Loss of structural integrity of any component associated with an overhead line supported on Steel Tower, excluding any associated Tower mounted plant, such that the residual strength of the component required immediate intervention. | Loss of structural integrity of any component associated with an overhead line supported on the Tower, excluding any associated Tower mounted plant, such that the residual strength of the component required intervention within a prescribed timescale. | Cracked insulator | Loss of protection. Loss of plant. Earthing. Any issues relating to the support, safety notices and anti-climbing guards. Conductor icing which does not result in permanent damage to the conductor. Cable boxes and platforms (including sealing ends).
Pressurised Cable | Carry load and fault current safely and reliably, without overheating or causing damage to the environment. | Oil or Gas leak / Top up. Cable Fault. Joint Failure. | Cable Fault. Joint Fault. | Accessory or joint failure causing loss of fluid. | Pressure gauges. Sheath deterioration. | Sheath damage and or repair. Third party damages.
Submarine Cables | Carry load and fault current safely and reliably, without overheating or causing damage to the environment. | Cable Fault. Joint Failure. | Cable Fault. Joint Fault. | N/A | N/A | Sheath damage and or repair. Third party damages
Non Pressurised Cable | Carry load and fault current safely and reliably, without overheating or causing damage to the environment. | Cable fault. Joint failure. | Cable Fault. Joint Fault. | N/A | N/A | Sheath damage and or repair. Third party damages.
Concrete Structures | Carries a piece of switchgear and is an integral part of the plant. This excludes plinths for plant which is designed with legs or other types of support for the operable parts of the plant and all power transformers. | Loss of residual strength or loss of stability. | Failure of the structure resulting in the plant item becoming unstable, the plant tilts or in any other way cannot be operated as a result of the condition of the concrete. | Loss of section. Cracking and spilling of the concrete such that the residual strength is between 80 and 100% of current condition. | Loss of chemical structure and hence reduction in strength. | Plinths. Auxiliary structures not made of concrete. Busbar supports.

## 20
Asset Register Category | Sub-division | Normal Expected Life
LV Poles | Concrete | 60
LV Poles | Steel | 50
LV Poles | Wood | 55
LV Poles | Other (e.g. fibreglass) | 80
LV Circuit Breaker |  | 60
LV Pillar (ID) |  | 60
LV Pillar (OD at Substation) |  | 60
LV Pillar (OD not at a Substation) |  | 60
LV Board (WM) |  | 60
LV UGB |  | 55
LV Board (X-type Network) (WM) |  | 60
6.6/11kV Poles | Concrete | 60
6.6/11kV Poles | Steel | 50
6.6/11kV Poles | Wood | 55
6.6/11kV Poles | Other (e.g. fibreglass) | 80
20kV Poles | Concrete | 60
20kV Poles | Steel | 50
20kV Poles | Wood | 55
20kV Poles | Other (e.g. fibreglass) | 80
HV Sub Cable |  | 60
6.6/11kV CB (GM) Primary |  | 55
6.6/11kV CB (GM) Secondary |  | 55
6.6/11kV Switch (GM) |  | 55
6.6/11kV RMU |  | 55
6.6/11kV X-type RMU |  | 55
20kV CB (GM) Primary |  | 55
20kV CB (GM) Secondary |  | 55
20kV Switch (GM) |  | 55
20kV RMU |  | 55
6.6/11kV Transformer (GM) |  | 60
20kV Transformer (GM) |  | 60
33kV Pole | Concrete | 60
33kV Pole | Steel | 50
33kV Pole | Wood | 55
33kV Pole | Other (e.g. fibreglass) | 80
66kV Pole | Concrete | 60
66kV Pole | Steel | 50
66kV Pole | Wood | 55
66kV Pole | Other (e.g. fibreglass) | 80
33kV OHL (Tower Line) Conductor | ACSR - greased | 55
33kV OHL (Tower Line) Conductor | ACSR - non-greased | 50
33kV OHL (Tower Line) Conductor | AAAC | 60
33kV OHL (Tower Line) Conductor | Cad Cu | 50
33kV OHL (Tower Line) Conductor | Cu | 70
33kV OHL (Tower Line) Conductor | Other | 50
33kV Tower | Steelwork | 80
33kV Tower | Foundation - Fully Encased Concrete | 95
33kV Tower | Foundation - Earth Grillage | 60
33kV Tower | Paint System - Galvanising | 30
33kV Tower | Paint System - Paint | 20
33kV Fittings |  | 40
66kV OHL (Tower Line) Conductor | ACSR - greased | 55
66kV OHL (Tower Line) Conductor | ACSR - non-greased | 50
66kV OHL (Tower Line) Conductor | AAAC | 60
66kV OHL (Tower Line) Conductor | Cad Cu | 50
66kV OHL (Tower Line) Conductor | Cu | 70
66kV OHL (Tower Line) Conductor | Other | 50
66kV Tower | Steelwork | 80
66kV Tower | Foundation - Fully Encased Concrete | 95
66kV Tower | Foundation - Earth Grillage | 60
66kV Tower | Paint System - Galvanising | 30
66kV Tower | Paint System - Paint | 20
66kV Fittings |  | 40
33kV UG Cable (Non Pressurised) | Aluminium sheath - Aluminium conductor | 100
33kV UG Cable (Non Pressurised) | Aluminium sheath - Copper conductor | 100
33kV UG Cable (Non Pressurised) | Lead sheath - Aluminium conductor | 100
33kV UG Cable (Non Pressurised) | Lead sheath - Copper conductor | 100
33kV UG Cable (Oil) | Aluminium sheath - Aluminium conductor | 75
33kV UG Cable (Oil) | Aluminium sheath - Copper conductor | 75
33kV UG Cable (Oil) | Lead sheath - Aluminium conductor | 80
33kV UG Cable (Oil) | Lead sheath - Copper conductor | 80
33kV UG Cable (Gas) | Aluminium sheath - Aluminium conductor | 65
33kV UG Cable (Gas) | Aluminium sheath - Copper conductor | 70
33kV UG Cable (Gas) | Lead sheath - Aluminium conductor | 75
33kV UG Cable (Gas) | Lead sheath - Copper conductor | 75
66kV UG Cable (Non Pressurised) | Aluminium sheath - Aluminium conductor | 100
66kV UG Cable (Non Pressurised) | Aluminium sheath - Copper conductor | 100
66kV UG Cable (Non Pressurised) | Lead sheath - Aluminium conductor | 100
66kV UG Cable (Non Pressurised) | Lead sheath - Copper conductor | 100
66kV UG Cable (Oil) | Aluminium sheath - Aluminium conductor | 75
66kV UG Cable (Oil) | Aluminium sheath - Copper conductor | 75
66kV UG Cable (Oil) | Lead sheath - Aluminium conductor | 80
66kV UG Cable (Oil) | Lead sheath - Copper conductor | 80
66kV UG Cable (Gas) | Aluminium sheath - Aluminium conductor | 65
66kV UG Cable (Gas) | Aluminium sheath - Copper conductor | 70
66kV UG Cable (Gas) | Lead sheath - Aluminium conductor | 75
66kV UG Cable (Gas) | Lead sheath - Copper conductor | 75
EHV Sub Cable |  | 60
33kV CB (Air Insulated Busbars)(ID) (GM) |  | 60
33kV CB (Air Insulated Busbars)(OD) (GM) |  | 50
33kV CB (Gas Insulated Busbars)(ID)(GM) |  | 60
33kV CB (Gas Insulated Busbars)(OD)(GM) |  | 50
33kV Switch (GM) |  | 55
33kV RMU |  | 55
66kV CB (Air Insulated Busbars)(ID) (GM) |  | 50
66kV CB (Air Insulated Busbars)(OD) (GM) |  | 55
66kV CB (Gas Insulated Busbars)(ID)(GM) |  | 55
66kV CB (Gas Insulated Busbars)(OD)(GM) |  | 50
33kV Transformer (GM) | Transformer - Pre 1980 | 60
33kV Transformer (GM) | Transformer - Post 1980 | 50
33kV Transformer (GM) | Tapchanger | 60
66kV Transformer (GM) | Transformer - Pre 1980 | 60
66kV Transformer (GM) | Transformer - Post 1980 | 50
66kV Transformer (GM) | Tapchanger | 60
132kV OHL (Tower Line) Conductor | ACSR - greased | 55
132kV OHL (Tower Line) Conductor | ACSR - non-greased | 50
132kV OHL (Tower Line) Conductor | AAAC | 60
132kV OHL (Tower Line) Conductor | Cad Cu | 50
132kV OHL (Tower Line) Conductor | Cu | 70
132kV OHL (Tower Line) Conductor | Other | 50
132kV Tower | Steelwork | 80
132kV Tower | Foundation - Fully Encased Concrete | 95
132kV Tower | Foundation - Earth Grillage | 60
132kV Tower | Paint System - Galvanising | 30
132kV Tower | Paint System - Paint | 20
132kV Fittings |  | 40
132kV UG Cable (Non Pressurised) | Aluminium sheath - Aluminium conductor | 100
132kV UG Cable (Non Pressurised) | Aluminium sheath - Copper conductor | 100
132kV UG Cable (Non Pressurised) | Lead sheath - Aluminium conductor | 100
132kV UG Cable (Non Pressurised) | Lead sheath - Copper conductor | 100
132kV UG Cable (Oil) | Aluminium sheath - Aluminium conductor | 75
132kV UG Cable (Oil) | Aluminium sheath - Copper conductor | 75
132kV UG Cable (Oil) | Lead sheath - Aluminium conductor | 80
132kV UG Cable (Oil) | Lead sheath - Copper conductor | 80
132kV UG Cable (Gas) | Aluminium sheath - Aluminium conductor | 65
132kV UG Cable (Gas) | Aluminium sheath - Copper conductor | 70
132kV UG Cable (Gas) | Lead sheath - Aluminium conductor | 75
132kV UG Cable (Gas) | Lead sheath - Copper conductor | 75
132kV Sub Cable |  | 60
132kV CB (Air Insulated Busbars)(ID) (GM) |  | 60
132kV CB (Air Insulated Busbars)(OD) (GM) |  | 50
132kV CB (Gas Insulated Busbars)(ID) (GM) |  | 60
132kV CB (Gas Insulated Busbars)(OD) (GM) |  | 55
132kV Transformer (GM) | Transformer - Pre 1980 | 60
132kV Transformer (GM) | Transformer - Post 1980 | 50
132kV Transformer (GM) | Tapchanger | 60

## 21
Functional Failure Category | K-Value (%) | C-Value | Health Score Limit
LV UGB | 0.0077 | 1.087 | 4
LV Circuit Breaker | 0.0041 | 1.087 | 4
LV Pillar (ID) | 0.0046 | 1.087 | 4
LV Pillar (OD at Substation) / LV Pillar (OD not at a Substation) | 0.0046 | 1.087 | 4
LV Board (WM) | 0.0069 | 1.087 | 4
HV Switchgear (GM) - Primary | 0.0052 | 1.087 | 4
HV Switchgear (GM) - Distribution (GM) | 0.0067 | 1.087 | 4
EHV Switchgear (GM) (33kV & 22kV assets only) | 0.0223 | 1.087 | 4
EHV Switchgear (GM) (66kV assets only) | 0.0512 | 1.087 | 4
132kV CBs | 0.0431 | 1.087 | 4
HV Transformer (GM) | 0.0078 | 1.087 | 4
EHV Transformer/ 132kV Transformer | 0.0454 | 1.087 | 4
Poles | 0.0285 | 1.087 | 4
Towers | 0.0545 | 1.087 | 4
Fittings | 0.0096 | 1.087 | 4
OHL Conductor | 0.008 | 1.087 | 4
Pressurised Cable (EHV UG Cable (Oil) and 132kV UG Cable (Oil)) | 2.0944 | 1.087 | 4
Pressurised Cable (EHV UG Cable (Gas) and 132kV UG Cable (Gas)) | 4.5036 | 1.087 | 4
Submarine Cables | 0.0202 | 1.087 | 4
Non Pressurised Cable | 0.0658 | 1.087 | 4

## 22
Lower | Upper | Bound Description | Switchgear | Transformers | Poles (Wood) | Poles (Steel) | Poles (Concrete) | Towers (Structure) | Towers (Fittings) | Towers (Conductor)
0 | 1 | Distance from Coast Banding (km) | 1.35 | 1.35 | 1 | 1.5 | 1.25 | 1.8 | 2 | 2
1 | 5 | Distance from Coast Banding (km) | 1.1 | 1.1 | 1 | 1.2 | 1.1 | 1.45 | 1.5 | 1.5
5 | 10 | Distance from Coast Banding (km) | 1.05 | 1.05 | 1 | 1.1 | 1.05 | 1.2 | 1.2 | 1.2
10 | 20 | Distance from Coast Banding (km) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
20 |  | Distance from Coast Banding (km) | 0.9 | 0.9 | 1 | 1 | 1 | 0.85 | 1 | 1
Default | Default | Distance from Coast Banding (km) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1

## 23
Lower | Upper | Bound Description | Switchgear | Transformers | Poles (Wood) | Poles (Steel) | Poles (Concrete) | Towers (Structure) | Towers (Fittings) | Towers (Conductor)
0 | 100 | Altitude From Sea Level Banding (m) | 0.9 | 0.9 | 1 | 1 | 1 | 0.9 | 0.95 | 0.95
100 | 200 | Altitude From Sea Level Banding (m) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
200 | 300 | Altitude From Sea Level Banding (m) | 1.05 | 1.05 | 1 | 1 | 1 | 1.15 | 1.05 | 1.05
300 |  | Altitude From Sea Level Banding (m) | 1.1 | 1.1 | 1 | 1 | 1 | 1.3 | 1.15 | 1.15
Default | Default | Altitude From Sea Level Banding (m) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1

## 24
Corrosion Category Index | Switchgear | Transformers | Poles (Wood) | Poles (Steel) | Poles (Concrete) | Towers (Structure) | Towers (Fittings) | Towers (Conductor)
1 | 0.9 | 0.9 | 1 | 0.9 | 0.9 | 0.75 | 0.95 | 0.95
2 | 0.95 | 0.95 | 1 | 0.95 | 0.95 | 0.9 | 0.95 | 0.95
3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
4 | 1.1 | 1.1 | 1 | 1.15 | 1.05 | 1.3 | 1.05 | 1.05
5 | 1.25 | 1.25 | 1 | 1.35 | 1.1 | 1.6 | 1.2 | 1.2
Default | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1

## 25
Increment Constant | Switchgear | Transformers | Submarine Cables | Poles (Wood) | Poles (Steel) | Poles (Concrete) | Towers (Structure) | Towers (Fittings) | Towers (Conductor)
INC | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0

## 25A
Asset Register Category | Default 'environment' to be assumed when deriving Location Factor
LV Poles | Outdoor
LV Circuit Breaker | Indoor
LV Pillar (ID) | Indoor
LV Pillar (OD at Substation) | Outdoor
LV Pillar (OD not at a Substation) | Outdoor
LV Board (WM) | Indoor
LV UGB | n/a
LV Board (X-type Network) (WM) | Indoor
6.6/11kV Poles | Outdoor
20kV Poles | Outdoor
HV Sub Cable | n/a
6.6/11kV CB (GM) Primary | Indoor
6.6/11kV CB (GM) Secondary | Indoor
6.6/11kV Switch (GM) | Indoor
6.6/11kV RMU | Indoor
6.6/11kV X-type RMU | Indoor
20kV CB (GM) Primary | Indoor
20kV CB (GM) Secondary | Indoor
20kV Switch (GM) | Indoor
20kV RMU | Indoor
6.6/11kV Transformer (GM) | Indoor
20kV Transformer (GM) | Indoor
33kV Pole | Outdoor
66kV Pole | Outdoor
33kV OHL (Tower Line) Conductor | Outdoor
33kV Tower | Outdoor
33kV Fittings | Outdoor
66kV OHL (Tower Line) Conductor | Outdoor
66kV Tower | Outdoor
66kV Fittings | Outdoor
33kV UG Cable (Non Pressurised) | n/a
33kV UG Cable (Oil) | n/a
33kV UG Cable (Gas) | n/a
66kV UG Cable (Non Pressurised) | n/a
66kV UG Cable (Oil) | n/a
66kV UG Cable (Gas) | n/a
EHV Sub Cable | n/a
33kV CB (Air Insulated Busbars)(ID) (GM) | Indoor
33kV CB (Air Insulated Busbars)(OD) (GM) | Outdoor
33kV CB (Gas Insulated Busbars)(ID)(GM) | Indoor
33kV CB (Gas Insulated Busbars)(OD)(GM) | Outdoor
33kV Switch (GM) | Indoor
33kV RMU | Indoor
66kV CB (Air Insulated Busbars)(ID) (GM) | Indoor
66kV CB (Air Insulated Busbars)(OD) (GM) | Outdoor
66kV CB (Gas Insulated Busbars)(ID)(GM) | Indoor
66kV CB (Gas Insulated Busbars)(OD)(GM) | Outdoor
33kV Transformer (GM) | Outdoor
66kV Transformer (GM) | Outdoor
132kV OHL (Tower Line) Conductor | Outdoor
132kV Tower | Outdoor
132kV Fittings | Outdoor
132kV UG Cable (Non Pressurised) | n/a
132kV UG Cable (Oil) | n/a
132kV UG Cable (Gas) | n/a
132kV Sub Cable | n/a
132kV CB (Air Insulated Busbars)(ID) (GM) | Indoor
132kV CB (Air Insulated Busbars)(OD) (GM) | Outdoor
132kV CB (Gas Insulated Busbars)(ID) (GM) | Indoor
132kV CB (Gas Insulated Busbars)(OD) (GM) | Outdoor
132kV Transformer (GM) | Outdoor

## 26
Topography | Score (Sea) | Score (Land locked)
Low Detrimental Topography | 1.25 | 0.5
Medium Detrimental Topography | 1.5 | 0.6
High Detrimental Topography | 2.25 | 0.9
Very High Detrimental Topography | 3 | 1.2
Default | 1.25 | 0.5

## 27
Situation | Score
Laid on bed | 1
Covered | 0.9
Buried | 0.8
Default | 1

## 28
Rating | Description | Score
1 | Sheltered sea loch, Wind <200 W/m2 | 1
2 | Wave <15kW/m, Wind 200-800 W/m2 | 1.2
3 | Wave >15kW/m, Wind > 800 W/m2 | 1.4
| Default | 1

## 29
Intensity | Scoring (Sea) | Scoring (Landlocked)
Low | 1.1 | 1
Moderate | 1.25 | 1.15
High | 1.5 | 1.4
Default | 1.1 | 1

## 30
Duty Factor 1 | Lower | Upper | Bound Description | Duty Factor (LV & HV) | Duty Factor (EHV & 132kV)
DF1 | 0 | 50 | Maximum % Utilisation under normal operating conditions | 0.8 | 1
DF1 | 50 | 70 | Maximum % Utilisation under normal operating conditions | 0.9 | 1.1
DF1 | 70 | 100 | Maximum % Utilisation under normal operating conditions | 1 | 1.3
DF1 | 100 |  | Maximum % Utilisation under normal operating conditions | 1.8 | 2
DF1 | Default | Default | Maximum % Utilisation under normal operating conditions | 1 | 1

## 30A
Duty Factor 2 | Lower | Upper | Bound Description | Duty Factor
DF2 | 0 | 40 | Operating Voltage / Design Voltage (%) | 0.7
DF2 | 40 | 55 | Operating Voltage / Design Voltage (%) | 0.8
DF2 | 55 | 70 | Operating Voltage / Design Voltage (%) | 0.9
DF2 | 70 |  | Operating Voltage / Design Voltage (%) | 1
DF2 | Default | Default | Operating Voltage / Design Voltage (%) | 1

## 31
Number of operations | Duty Factor
Normal/Low | 1
High (eg: Auto-reclosers) | 1.2
Default | 1

## 32
Lower | Upper | Bound Description | Duty Factor
0 | 50 | Max % Utilisation under normal operating conditions | 0.9
50 | 70 | Max % Utilisation under normal operating conditions | 0.95
70 | 100 | Max % Utilisation under normal operating conditions | 1
100 |  | Max % Utilisation under normal operating conditions | 1.4
Default | Default | Max % Utilisation under normal operating conditions | 1

## 33
Lower | Upper | Bound Description | Duty Factor
0 | 50 | Max % Utilisation under normal operating conditions (Transformer) | 1
50 | 70 | Max % Utilisation under normal operating conditions (Transformer) | 1.05
70 | 100 | Max % Utilisation under normal operating conditions (Transformer) | 1.1
100 |  | Max % Utilisation under normal operating conditions (Transformer) | 1.4
Default | Default | Max % Utilisation under normal operating conditions (Transformer) | 1
0 | 7 | Average Number of Daily Taps (TapChanger) | 0.9
7 | 14 | Average Number of Daily Taps (TapChanger) | 1
14 | 28 | Average Number of Daily Taps (TapChanger) | 1.2
28 |  | Average Number of Daily Taps (TapChanger) | 1.3
Default | Default | Average Number of Daily Taps (TapChanger) | 1

## 34
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.9 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. Minor corrosion | 1.2 | 10 | 0.5
Substantial Deterioration | e.g. Major corrosion | 1.4 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 35
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
None | Dry | 1 | 10 | 0.5
Present in Pit | Evidence of moisture observed in pit | 1.1 | 10 | 0.5
Present in Bell Housing | Evidence of moisture observed in bell housing | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 36
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Satisfactory | No observed deterioration | 0.9 | 10 | 0.5
Some Deterioration | e.g. Minor corrosion | 1.2 | 10 | 0.5
Substantial Deterioration | e.g. Major corrosion | 1.4 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 37
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration | No observed deterioration | 0.9 | 10 | 0.5
Minor Deterioration | Chips and advanced aging | 1 | 10 | 0.5
Major Deterioration | Evidence of flashover or damage, or degradation of insulation material | 1.3 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 38
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration | No observed deterioration | 0.9 | 10 | 0.5
Minor Deterioration | Observed running higher than ambient | 1 | 10 | 0.5
Major Deterioration | Evidence of overheating | 1.5 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 39
Condition Criteria: Phase barriers Present? | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Yes | Phase Barriers Present | 1 | 10 | 0.5
Missing | Phase Barriers Not Present (in whole or part) | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 40
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.9 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. Minor corrosion | 1.3 | 10 | 0.5
Substantial Deterioration | e.g. Major corrosion | 1.6 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 41
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.9 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. Minor corrosion | 1.2 | 10 | 0.5
Substantial Deterioration | e.g. Major corrosion | 1.4 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 42
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Good | No leakage | 0.9 | 10 | 0.5
Slight leak | Evidence of slight compound leak | 1 | 10 | 0.5
Poor | Significant compound leak | 1.1 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 44
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.9 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. Minor corrosion | 1.2 | 10 | 0.5
Substantial Deterioration | Visible holes in casing or structurally unsound | 1.4 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 43
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.9 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. Minor corrosion | 1.2 | 10 | 0.5
Substantial Deterioration | Degradation of insulation material | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 45
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Good | No leakage | 0.9 | 10 | 0.5
Slight leak | Evidence of slight compound leak | 1 | 10 | 0.5
Poor | Significant compound leak | 1.1 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 46
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.9 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. Minor corrosion | 1.2 | 10 | 0.5
Substantial Deterioration | Degradation of insulation material | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 47
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Satisfactory | No observed deterioration | 0.9 | 10 | 0.5
Some Deterioration | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Substantial Deterioration | Degradation of insulation material | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 48
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration | No obvious degradation | 1 | 10 | 0.5
Minor Deterioration | Observed running higher than ambient | 1.2 | 10 | 0.5
Major Deterioration | Evidence of overheating | 1.5 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 49
Condition Criteria: Phase barriers Present? | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Yes | Phase Barriers Present | 1 | 10 | 0.5
Missing | Phase Barriers Not Present (in whole or part) | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 50
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.9 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. Minor corrosion or evidence of low level oil leaks (If appropriate) | 1.2 | 10 | 0.5
Substantial Deterioration | Severe corrosion (e.g. holes) | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 51
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Good | Oil: No leakage, Gas: Pressure within acceptable range | 0.9 | 10 | 0.5
Slight leak | Oil: Slight weep, Gas: Not used | 1 | 10 | 0.5
Poor | Oil: Free oil observed, Gas: Pressure outside of acceptable range | 1.1 | 10 | 0.5
Severe leak | Severe unrepairable leak and/or repeated gas top-ups | 1.3 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 52
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Ambient or Below | At or below ambient temperature | 0.9 | 10 | 0.5
Above ambient | Above ambient temperature | 1 | 10 | 0.5
Substantially above ambient | Operating above the manufacturers recommended maximum temperature | 1.1 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 53
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.9 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. Minor corrosion or evidence of low level oil leaks (If appropriate) | 1.2 | 10 | 0.5
Substantial Deterioration | e.g. observed or potential mechanism defect, internal insulation, etc | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 54
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Better than expected | Air conditioned | 0.9 | 10 | 0.5
As Expected | This is an environment which is typified as dry and has a degree of background heating or dehumidification which maintains this year round. | 1 | 10 | 0.5
Deteriorated Environment | Heating or dehumidification faulty; room temperature is hotter than recommended by environmental policy; condensation evident in switch room etc. | 1.3 | 10 | 0.5
Severely Deteriorated Environment | No heating or dehumidification installed; room temperature is excessively hot; roof or structure permits water ingress; water stands in trenches or free water is observed in the switch room. | 1.5 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 55
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.9 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. Minor corrosion or evidence of low level oil leaks (If appropriate) | 1.2 | 10 | 0.5
Substantial Deterioration | Severe corrosion (e.g. holes) | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 56
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Good | Oil: No leakage, Gas: Pressure within acceptable range | 0.9 | 10 | 0.5
Slight leak | Oil: Slight weep, Gas: Not used | 1 | 10 | 0.5
Poor | Oil: Free oil observed, Gas: Pressure outside of acceptable range | 1.1 | 10 | 0.5
Severe leak | Severe unrepairable leak and/or repeated gas top-ups | 1.3 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 57
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Ambient or Below | At or below ambient temperature | 0.9 | 10 | 0.5
Above Ambient | Above ambient temperature | 1 | 10 | 0.5
Substantially Above Ambient | Operating above the manufacturers recommended maximum temperature | 1.1 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 58
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.9 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. Minor corrosion or evidence of low level oil leaks (If appropriate) | 1.2 | 10 | 0.5
Substantial Deterioration | e.g. observed or potential mechanism defect, internal insulation, etc. | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 59
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Better than Expected | Air conditioned | 0.9 | 10 | 0.5
As Expected | This is an environment which is typified as dry and has a degree of background heating or dehumidification which maintains this year round. | 1 | 10 | 0.5
Deteriorated Environment | Heating or dehumidification faulty; room temperature is hotter than recommended by environmental policy; condensation evident in switch room etc. | 1.3 | 10 | 0.5
Severely Deteriorated Environment | No heating or dehumidification installed; room temperature is excessively hot; roof or structure permits water ingress; water stands in trenches or free water is observed in the switch room. | 1.5 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 60
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.9 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. Minor corrosion or evidence of low level oil leaks (If appropriate) | 1.2 | 10 | 0.5
Substantial Deterioration | Severe corrosion (e.g. holes) | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 61
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Good | Oil: No leakage, Gas: Pressure within acceptable range | 0.9 | 10 | 0.5
Slight Leak | Oil: Slight weep, Gas: Not used | 1 | 10 | 0.5
Poor | Oil: Free oil observed, Gas: Pressure outside of acceptable range | 1.1 | 10 | 0.5
Severe Leak | Severe unrepairable leak and/or repeated gas top-ups | 1.3 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 62
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Ambient or Below | At or below ambient temperature | 0.9 | 10 | 0.5
Above Ambient | Above ambient temperature | 1 | 10 | 0.5
Substantially Above Ambient | Operating above the manufacturers recommended maximum temperature | 1.1 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 63
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.9 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. Minor corrosion or evidence of low level oil leaks (If appropriate) | 1.2 | 10 | 0.5
Substantial Deterioration | e.g. observed or potential mechanism defect, internal insulation, etc. | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 64
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Better than Expected | Air conditioned | 0.9 | 10 | 0.5
As Expected | This is an environment which is typified as dry and has a degree of background heating or dehumidification which maintains this year round. | 1 | 10 | 0.5
Deteriorated Environment | Heating or dehumidification faulty; room temperature is hotter than recommended by environmental policy; condensation evident in switch room etc. | 1.3 | 10 | 0.5
Severely Deteriorated Environment | No heating or dehumidification installed; room temperature is excessively hot; roof or structure permits water ingress; water stands in trenches or free water is observed in the switch room. | 1.5 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 65
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration |  | 0.9 | 10 | 0.5
Normal Wear | Concrete Structures: Surface Deterioration, Steel Structures: Minor localised surface corrosion | 1 | 10 | 0.5
Some Deterioration | Concrete Structures: Minor cracks and loss of section, Steel Structures: Some significant corrosion, minor loss of cross section | 1.3 | 10 | 0.5
Substantial Deterioration | Concrete Structures: Loss of section, reinforcing exposed, Steel Structures: Major corrosion, wasting of steel cross section, laminated rusk, holes or loss of steel at edges, severe damage | 1.5 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 66
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.9 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. Minor corrosion or evidence of low level oil leaks (If appropriate) | 1.2 | 10 | 0.5
Substantial Deterioration | Severe corrosion (e.g. holes) | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 67
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Good | Oil: No leakage, Gas: Pressure within acceptable range | 0.9 | 10 | 0.5
Slight leak | Oil: Slight weep, Gas: Not used | 1 | 10 | 0.5
Poor | Oil: Free oil observed, Gas: Pressure outside of acceptable range | 1.1 | 10 | 0.5
Severe leak | Severe unrepairable leak and/or repeated gas top-ups | 1.3 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 68
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Ambient or Below | At or below ambient temperature | 0.9 | 10 | 0.5
Above Ambient | Above ambient temperature | 1 | 10 | 0.5
Substantially Above Ambient | Operating above the manufacturers recommended maximum temperature | 1.1 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 69
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.9 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. Minor corrosion or evidence of low level oil leaks (If appropriate) | 1.2 | 10 | 0.5
Substantial Deterioration | e.g. observed or potential mechanism defect, internal insulation, etc. | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 70
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Better than Expected | Air conditioned | 0.9 | 10 | 0.5
As Expected | This is an environment which is typified as dry and has a degree of background heating or dehumidification which maintains this year round. | 1 | 10 | 0.5
Deteriorated Environment | Heating or dehumidification faulty; room temperature is hotter than recommended by the environmental policy; condensation evident in switch room etc. | 1.3 | 10 | 0.5
Severely Deteriorated Environment | No heating or dehumidification installed; room temperature is excessively hot; roof or structure permits water ingress; water stands in trenches or free water is observed in the switch room. | 1.5 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 71
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration |  | 0.9 | 10 | 0.5
Normal Wear | Concrete Structures: Surface Deterioration, Steel Structures: Minor localised surface corrosion | 1 | 10 | 0.5
Some Deterioration | Concrete Structures: Minor cracks and loss of section, Steel Structures: Some significant corrosion, minor loss of cross section | 1.3 | 10 | 0.5
Substantial Deterioration | Concrete Structures: Loss of section, reinforcing exposed, Steel Structures: Major corrosion, wasting of steel cross section, laminated rusk, holes or loss of steel at edges, severe damage | 1.5 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 72
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration | No observed deterioration | 0.9 | 10 | 0.5
Minor Deterioration | Minor surface corrosion observed on observable pipe work | 1 | 10 | 0.5
Minor Air Losses | System runs excessively to maintain pressure | 1.3 | 10 | 0.5
Major Air Losses | Loss of pressure pipe section observed. Air leaks can be found by inspection; Certification Certificate notes defects. Etc. | 1.5 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 73
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | Condition as new | 0.9 | 10 | 0.5
Good | e.g. no evidence of corrosion or oil leakage | 1 | 10 | 0.5
Slight Deterioration | e.g. minor localised surface corrosion, no evidence of oil leakage or slight (but repairable) oil leakage | 1.1 | 10 | 0.5
Poor | e.g. some significant corrosion, or evidence of slight oil (unrepairable) leakage | 1.25 | 10 | 0.5
Very Poor | e.g. major corrosion or evidence of significant oil leakage | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 74
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion or evidence of low level oil leaks (If appropriate) | 1.4 | 10 | 0.5
Substantial Deterioration | e.g. major corrosion or evidence of significant oil leakage | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 75
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion or evidence of low level oil leaks (If appropriate) | 1.2 | 10 | 0.5
Substantial Deterioration | e.g. major corrosion or evidence of significant oil leakage | 1.4 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 76
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion or evidence of low level oil leaks (If appropriate) | 1.2 | 10 | 0.5
Substantial Deterioration | e.g. visible cracks, damage, surface degradation and/or leakage | 1.4 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 77
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Normal Wear | The asset component exhibits some deterioration but is fit for continued service. There is no or little obvious signs of corrosion | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion | 1.1 | 10 | 0.5
Substantial Deterioration | e.g. major corrosion | 1.2 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 78
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion or evidence of compound leaks (where appropriate) | 1.1 | 10 | 0.5
Substantial Deterioration | e.g major corrosion | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 79
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion or evidence of low level oil leaks (If appropriate) | 1.4 | 10 | 0.5
Substantial Deterioration | e.g. major corrosion or evidence of significant oil leakage | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 80
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion or evidence of low level oil leaks (If appropriate) | 1.2 | 10 | 0.5
Substantial Deterioration | e.g. observed or potential mechanism defect, internal insulation, etc. | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 81
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.9 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion or wear to components | 1.2 | 10 | 0.5
Substantial Deterioration | e.g. major corrosion or excessive wear in component and bearings | 1.4 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 82
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.95 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion or wear | 1.1 | 10 | 0.5
Substantial Deterioration | e.g. major corrosion or excessive wear in component and bearings | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 83
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.95 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion or wear | 1.05 | 10 | 0.5
Substantial Deterioration | e.g. major corrosion or fraying of braids | 1.1 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 84
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion or evidence of low level oil leaks (If appropriate) | 1.4 | 10 | 0.5
Substantial Deterioration | e.g. major corrosion or evidence of significant oil leakage | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 85
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion or evidence of low level oil leaks (If appropriate) | 1.2 | 10 | 0.5
Substantial Deterioration | e.g. major corrosion or evidence of significant oil leakage | 1.4 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 86
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion or evidence of low level oil leaks (If appropriate) | 1.2 | 10 | 0.5
Substantial Deterioration | e.g. visible cracks, damage, surface degradation and/or leakage | 1.4 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 87
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. Minor corrosion | 1.1 | 10 | 0.5
Substantial Deterioration | e.g. major corrosion or evidence of significant oil leakage | 1.2 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 88
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. Minor corrosion or evidence of compound leaks (where appropriate) | 1.1 | 10 | 0.5
Substantial Deterioration | e.g. Major corrosion or evidence of low level oil leaks (If appropriate) | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 89
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion or evidence of low level oil leaks (If appropriate) | 1.4 | 10 | 0.5
Substantial Deterioration | e.g. major corrosion or evidence of significant oil leakage | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 90
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion or evidence of low level oil leaks (If appropriate) | 1.2 | 10 | 0.5
Substantial Deterioration | e.g. observed or potential mechanism defect, internal insulation, etc+ | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 91
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.9 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion or wear to components | 1.2 | 10 | 0.5
Substantial Deterioration | e.g. major corrosion or excessive wear in component and bearings | 1.4 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 92
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.95 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion or wear | 1.1 | 10 | 0.5
Substantial Deterioration | e.g. major corrosion or excessive wear in component and bearings | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 93
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.95 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion or wear | 1.05 | 10 | 0.5
Substantial Deterioration | e.g. major corrosion or fraying of braids | 1.1 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 94
Condition Criteria | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Good | The asset component exhibits deterioration but is fit for continued service. | 1 | 10 | 0.5
Poor | e.g. visible damage to armour | 1.6 | 10 | 5.5
Critical | e.g. mechanical damage to cable armour, loss of armour | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 95
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Acceptable | No defects observed | 1 | 10 | 0.5
Some Deterioration | e.g. minor physical damage that will lead to loss of strength | 1.3 | 10 | 0.5
Substantial Deterioration | e.g. visible splits, cracks, major physical damage affecting strength | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 96
Condition Criteria: Pole Top Rot Present? | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No | No pole top rot observed | 1 | 10 | 0.5
Yes | Pole top rot is observed | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 97
Condition Criteria: Pole Leaning? | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No | The pole is vertical | 1 | 10 | 0.5
Yes | The pole is not vertical | 1.2 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 98
Condition Criteria: Bird/Animal Damage? | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No | There is no animal damage | 1 | 10 | 0.5
Yes | There is animal damage | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 99
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Acceptable | No defects observed | 1 | 10 | 0.5
Some Deterioration | e.g. minor physical damage that will lead to loss of strength | 1.3 | 10 | 0.5
Substantial Deterioration | e.g. visible splits, cracks, major physical damage affecting strength | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 100
Condition Criteria: Pole Top Rot Present? | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No | No pole top rot observed | 1 | 10 | 0.5
Yes | Pole top rot is observed | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 101
Condition Criteria: Pole Leaning? | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No | The pole is vertical | 1 | 10 | 0.5
Yes | The pole is not vertical | 1.2 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 102
Condition Criteria: Bird/Animal Damage? | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No | There is no animal damage | 1 | 10 | 0.5
Yes | There is animal damage | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 103
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Acceptable | No defects observed | 1 | 10 | 0.5
Some Deterioration | e.g. minor physical damage that will lead to loss of strength | 1.3 | 10 | 0.5
Substantial Deterioration | e.g. visible splits, cracks, major physical damage affecting strength | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 104
Condition Criteria: Pole Top Rot Present? | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No | No pole top rot observed | 1 | 10 | 0.5
Yes | Pole top rot is observed | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 105
Condition Criteria: Pole Leaning? | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No | The pole is vertical | 1 | 10 | 0.5
Yes | The pole is not vertical | 1.2 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 106
Condition Criteria: Bird/Animal Damage? | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No | There is no animal damage | 1 | 10 | 0.5
Yes | There is animal damage | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 107
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Acceptable |  | 1 | 10 | 0.5
Mechanically Unsafe | Signs of wasting of steel cross-section, laminated rust, holes or loss of steel at edges, severe damage - requires urgent replacement | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 108
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Acceptable |  | 1 | 10 | 0.5
Mechanically Unsafe | Signs of wasting of steel cross-section, laminated rust, holes or loss of steel at edges, severe damage - requires urgent replacement | 1.2 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 109
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Acceptable |  | 1 | 10 | 0.5
Mechanically Unsafe | Signs of wasting of steel cross-section, laminated rust, holes or loss of steel at edges, severe damage - requires urgent replacement | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 110
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Acceptable |  | 1 | 10 | 0.5
Mechanically Unsafe | Signs of wasting of steel cross-section, laminated rust, holes or loss of steel at edges, severe damage - requires urgent replacement | 1.2 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 111
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New |  | 1 | 6.4 | 0.5
Slight Rust Breakthrough | Slight rust breakthrough - up to 5% of surface area affected. | 1.1 | 6.4 | 0.5
Moderate Rust Breakthrough | Moderate rust breakthrough - between 5% and 20% of surface area affected, and/or pitted rust | 1.6 | 6.4 | 0.5
Severe Rust Breakthrough | Severe rust breakthrough - more than 20% of surface area affected, AND/OR damaged or bent steelwork, AND/OR any blistered paintwork with evidence of severe rust underneath, painting/attention required urgently. | 1.8 | 6.4 | 5.5
Default | No data available | 1 | 6.4 | 0.5

## 112
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.95 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion | 1.4 | 10 | 0.5
Substantial Deterioration | Insufficient integrity to support tower loading | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 113
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Acceptable |  | 1 | 10 | 0.5
Mechanically Unsafe | Signs of wasting of steel cross-section, laminated rust, holes or loss of steel at edges, severe damage - requires urgent replacement | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 114
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Acceptable |  | 1 | 10 | 0.5
Mechanically Unsafe | Signs of wasting of steel cross-section, laminated rust, holes or loss of steel at edges, severe damage - requires urgent replacement | 1.2 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 115
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Acceptable |  | 1 | 10 | 0.5
Mechanically Unsafe | Signs of wasting of steel cross-section, laminated rust, holes or loss of steel at edges, severe damage - requires urgent replacement | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 116
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Acceptable |  | 1 | 10 | 0.5
Mechanically Unsafe | Signs of wasting of steel cross-section, laminated rust, holes or loss of steel at edges, severe damage - requires urgent replacement | 1.2 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 117
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New |  | 1 | 6.4 | 0.5
Slight Rust Breakthrough | Slight rust breakthrough - up to 5% of surface area affected. | 1.1 | 6.4 | 0.5
Moderate Rust Breakthrough | Moderate rust breakthrough - between 5% and 20% of surface area affected, and/or pitted rust | 1.6 | 6.4 | 0.5
Severe Rust Breakthrough | Severe rust breakthrough - more than 20% of surface area affected, AND/OR damaged or bent steelwork, AND/OR any blistered paintwork with evidence of severe rust underneath, painting/attention required urgently. | 1.8 | 6.4 | 5.5
Default | No data available | 1 | 6.4 | 0.5

## 118
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.95 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion | 1.4 | 10 | 0.5
Substantial Deterioration | Insufficient integrity to support tower loading | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 119
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.9 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1.1 | 10 | 0.5
Some Deterioration | Partial Loss of required structural integrity | 1.3 | 10 | 0.5
Substantial Deterioration | Loss of required structural integrity | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 120
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.9 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1.1 | 10 | 0.5
Some Deterioration | Partial Loss of required Structural Integrity | 1.3 | 10 | 0.5
Substantial Deterioration | Loss of required structural integrity | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 121
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.9 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1.1 | 10 | 0.5
Some Deterioration | Partial Loss of required electrical Integrity | 1.3 | 10 | 0.5
Substantial Deterioration | Loss of required electrical integrity | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 122
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.9 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1.1 | 10 | 0.5
Some Deterioration | Partial Loss of required structural integrity | 1.3 | 10 | 0.5
Substantial Deterioration | Loss of required structural integrity | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 123
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.9 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1.1 | 10 | 0.5
Some Deterioration | Partial Loss of required Structural Integrity | 1.3 | 10 | 0.5
Substantial Deterioration | Loss of required structural integrity | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 124
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.9 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1.1 | 10 | 0.5
Some Deterioration | Partial Loss of required Structural Integrity | 1.3 | 10 | 0.5
Substantial Deterioration | Loss of required structural integrity | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 125
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.9 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1.1 | 10 | 0.5
Some Deterioration | Partial Loss of required electrical integrity | 1.3 | 10 | 0.5
Substantial Deterioration | Loss of required electrical integrity | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 126
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.9 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1.1 | 10 | 0.5
Some Deterioration | Partial Loss of required Structural Integrity | 1.3 | 10 | 0.5
Substantial Deterioration | Loss of required structural integrity | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 127
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.9 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1.1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion | 1.3 | 10 | 0.5
Substantial Deterioration | e.g. birdcaging, broken strands, loss of section | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 128
Condition Criteria: No. of Midspan Joints | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
0 | No joints in the span. A span includes all conductors in that span | 1 | 10 | 0.5
1 | 1 joint in the span | 1.05 | 10 | 0.5
2 | 2 joints in the span | 1.1 | 10 | 0.5
>2 | More than two joints in the span | 1.2 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 129
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | No observed deterioration | 0.9 | 10 | 0.5
Normal Wear | The asset component is fit for continued service. There is little deterioration | 1.1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion | 1.3 | 10 | 0.5
Substantial Deterioration | e.g. birdcaging, broken strands, loss of section | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 130
Condition Criteria: No. of Midspan Joints | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
0 | No joints in the span. A span includes all conductors in that span | 1 | 10 | 0.5
1 | 1 joint in the span | 1.05 | 10 | 0.5
2 | 2 joints in the span | 1.1 | 10 | 0.5
>2 | More than two joints in the span | 1.2 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 131
Condition Criteria: Operational Adequacy | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Operable | The LV UGB can be operated safely | 1 | 10 | 0.5
Inoperable | The LV UGB cannot be operated or repaired | 1.5 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 132
Condition Criteria: Operational Adequacy | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Acceptable | The device can be operated safely | 1 | 10 | 0.5
Unacceptable | The device cannot be operated safely | 1.6 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 133
Condition Criteria: Operational Adequacy | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Operable | The LV Board can be operated safely | 1 | 10 | 0.5
Inoperable - Secure | The LV Board cannot be operated but is physically secure | 1.3 | 10 | 0.5
Inoperable - Hazardous | The LV Board cannot be operated and presents a hazard to either operator, the public or both | 1.5 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 134
Condition Criteria: Security | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Satisfactory | The device can be operated safely | 1 | 10 | 0.5
Unsatisfactory | The device cannot be operated safely | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 135
Condition Criteria: Operational Adequacy | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Operable | The LV Pillar can be operated safely | 1 | 10 | 0.5
Inoperable - Secure | The LV Pillar cannot be operated but is physically secure | 1.3 | 10 | 0.5
Inoperable - Hazardous | The LV Pillar cannot be operated and presents a hazard to either operator, the public or both | 1.5 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 136
Condition Criteria: Partial Discharge Test Results | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | Low or negligible levels of partial discharge indicating no issues identified (e.g. a green condition using a TEV or <10% of manufacturers recommendation | 1 | 10 | 0.5
Medium | Some moderate levels of partial discharge recorded (e.g. ‘Amber’ result from TEV measuring device or between 10% and 30% of the manufacturers recommendation) | 1.1 | 10 | 0.5
High (Not Confirmed) | High levels of partial discharge indicating possible defect with plant / equipment, requiring further investigation (e.g. ‘Red’ result from TEV measuring device or above manufacturers recommendation) | 1.3 | 10 | 5.5
High (Confirmed) | High partial discharge. Source of partial discharge confirmed as potential source of failure | 1.5 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 137
Lower | Upper | Bound Description | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | As New | Condition Criteria: Ductor Test Results in % | The joint test result meets the manufacturers recommended value | 1 | 10 | 0.5
0 | 10 | Condition Criteria: Ductor Test Results, Deterioration from new in % | Up to 10% deterioration from the ‘As New’ condition | 1.1 | 10 | 0.5
10 |  | Condition Criteria: Ductor Test Results, Deterioration from new in % | Over 10% deterioration from the ‘As New’ condition | 1.3 | 10 | 0.5
Default | Default | Condition Criteria: Ductor Test Results | No data available | 1 | 10 | 0.5

## 138
Lower | Upper | Bound Description | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | As New | Condition Criteria: IR Test Results in % | The joint test result meets the manufacturers recommended value | 1 | 10 | 0.5
0 | 10 | Condition Criteria: IR Test Results, Deterioration from new in % | Up to 10% deterioration from the ‘As New’ condition | 1.1 | 10 | 0.5
10 |  | Condition Criteria: IR Test Results, Deterioration from new in % | Over 10% deterioration from the ‘As New’ condition | 1.3 | 10 | 0.5
Default | Default | Condition Criteria: IR Test Results | No data available | 1 | 10 | 0.5

## 139
Lower | Upper | Bound Description | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | As New | Condition Criteria: Oil Test Results in % | The oil test result meets the required European Standard for new oil | 1 | 10 | 0.5
0 | 10 | Condition Criteria: Oil Test Results, Deterioration from new in % | Up to 10% deterioration from the ‘As New’ condition | 1.1 | 10 | 0.5
10 |  | Condition Criteria: Oil Test Results, Deterioration from new in % | Over 10% deterioration from the ‘As New’ condition | 1.3 | 10 | 0.5
Default | Default | Condition Criteria: Oil Test Results | No data available | 1 | 10 | 0.5

## 140
Condition Criteria: Temperature Readings | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Ambient or Below | At or below ambient temperature | 0.9 | 10 | 0.5
Above ambient | Above ambient temperature | 1 | 10 | 0.5
Substantially above ambient | Operating above the manufacturers recommended maximum temperature | 1.1 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 141
Condition Criteria: Trip Timing Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Pass | Trip time within acceptable range for the type of switchgear | 1 | 10 | 0.5
Fail | Trip time slower than acceptable time for the type of switchgear | 1.4 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 142
Condition Criteria: Partial Discharge Test Results | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | Low or negligible levels of partial discharge indicating no issues identified (e.g. a green condition using a TEV or <10% of manufacturers recommendation | 1 | 10 | 0.5
Medium | Some moderate levels of partial discharge recorded (e.g. ‘Amber’ result from TEV measuring device or between 10% and 30% of the manufacturers recommendation) | 1.1 | 10 | 0.5
High (Not Confirmed) | High levels of partial discharge indicating possible defect with plant / equipment, requiring further investigation (e.g. ‘Red’ result from TEV measuring device or above manufacturers recommendation) | 1.3 | 10 | 5.5
High (Confirmed) | High partial discharge. Source of partial discharge confirmed as potential source of failure | 1.5 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 143
Lower | Upper | Bound Description | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | As New | Condition Criteria: Ductor Test Results in % | The joint test result meets the manufacturers recommended value | 1 | 10 | 0.5
0 | 10 | Condition Criteria: Ductor Test Results, Deterioration from new in % | Up to 10% deterioration from the ‘As New’ condition | 1.1 | 10 | 0.5
10 |  | Condition Criteria: Ductor Test Results, Deterioration from new in % | Over 10% deterioration from the ‘As New’ condition | 1.3 | 10 | 0.5
Default | Default | Condition Criteria: Ductor Test Results | No data available | 1 | 10 | 0.5

## 144
Lower | Upper | Bound Description | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | As New | Condition Criteria: Oil Test Results in % | The oil test result meets the required European Standard for new oil | 1 | 10 | 0.5
0 | 10 | Condition Criteria: Oil Test Results, Deterioration from new in % | Up to 10% deterioration from the ‘As New’ condition | 1.1 | 10 | 0.5
10 |  | Condition Criteria: Oil Test Results, Deterioration from new in % | Over 10% deterioration from the ‘As New’ condition | 1.3 | 10 | 0.5
Default | Default | Condition Criteria: Oil Test Results | No data available | 1 | 10 | 0.5

## 145
Condition Criteria: Temperature Readings | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Ambient or Below | At or below ambient temperature | 0.9 | 10 | 0.5
Above Ambient | Above ambient temperature | 1 | 10 | 0.5
Substantially Above Ambient | Operating above the manufacturers recommended maximum temperature | 1.1 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 146
Condition Criteria: Trip Timing Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Pass | Trip time within acceptable range for the type of switchgear | 1 | 10 | 0.5
Fail | Trip time slower than acceptable time for the type of switchgear | 1.4 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 147
Condition Criteria: Partial Discharge Test Results | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | Low or negligible levels of partial discharge indicating no issues identified (e.g. a green condition using a TEV or <10% of manufacturers recommendation | 1 | 10 | 0.5
Medium | Some moderate levels of partial discharge recorded (e.g. ‘Amber’ result from TEV measuring device or between 10% and 30% of the manufacturers recommendation) | 1.1 | 10 | 0.5
High (Not Confirmed) | High levels of partial discharge indicating possible defect with plant / equipment, requiring further investigation (e.g. ‘Red’ result from TEV measuring device or above manufacturers recommendation) | 1.3 | 10 | 5.5
High (Confirmed) | High partial discharge. Source of partial discharge confirmed as potential source of failure | 1.5 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 148
Lower | Upper | Bound Description | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | As New | Condition Criteria: Ductor Test Results in % | The joint test result meets the manufacturers recommended value | 1 | 10 | 0.5
0 | 10 | Condition Criteria: Ductor Test Results, Deterioration from new in % | Up to 10% deterioration from the ‘As New’ condition | 1.1 | 10 | 0.5
10 |  | Condition Criteria: Ductor Test Results, Deterioration from new in % | Over 10% deterioration from the ‘As New’ condition | 1.3 | 10 | 0.5
Default | Default | Condition Criteria: Ductor Test Results | No data available | 1 | 10 | 0.5

## 149
Lower | Upper | Bound Description | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | As New | Condition Criteria: IR Test Results in % | The insulation test result meets the manufacturers recommended value | 1 | 10 | 0.5
0 | 10 | Condition Criteria: IR Test Results, Deterioration from new in % | Up to 10% deterioration from the ‘As New’ condition | 1.1 | 10 | 0.5
10 |  | Condition Criteria: IR Test Results, Deterioration from new in % | Over 10% deterioration from the ‘As New’ condition | 1.3 | 10 | 0.5
Default | Default | Condition Criteria: IR Test Results | No data available | 1 | 10 | 0.5

## 150
Lower | Upper | Bound Description | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | As New | Condition Criteria: Oil Test Results in % | The oil or gas test result meets the required European Standard for new oil or gas | 1 | 10 | 0.5
0 | 10 | Condition Criteria: Oil Test Results, Deterioration from new in % | Up to 10% deterioration from the ‘As New’ condition | 1.1 | 10 | 0.5
10 |  | Condition Criteria: Oil Test Results, Deterioration from new in % | Over 10% deterioration from the ‘As New’ condition | 1.3 | 10 | 0.5
Default | Default | Condition Criteria: Oil Test Results | No data available | 1 | 10 | 0.5

## 151
Condition Criteria: Temperature Readings | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Ambient or Below | At or below ambient temperature | 0.9 | 10 | 0.5
Above Ambient | Above ambient temperature | 1 | 10 | 0.5
Substantially Above Ambient | Operating above the manufacturers recommended maximum temperature | 1.1 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 152
Condition Criteria: Trip Timing Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Pass | Trip time within acceptable range for the type of switchgear | 1 | 10 | 0.5
Fail | Trip time slower than acceptable time for the type of switchgear | 1.4 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 153
Condition Criteria: Partial Discharge Test Results | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | Low or negligible levels of partial discharge indicating no issues identified (e.g. a green condition using a TEV or <10% of manufacturers recommendation | 1 | 10 | 0.5
Medium | Some moderate levels of partial discharge recorded (e.g. ‘Amber’ result from TEV measuring device or between 10% and 30% of the manufacturers recommendation) | 1.1 | 10 | 0.5
High (Not Confirmed) | High levels of partial discharge indicating possible defect with plant / equipment, requiring further investigation (e.g. ‘Red’ result from TEV measuring device or above manufacturers recommendation) | 1.3 | 10 | 5.5
High (Confirmed) | High partial discharge. Source of partial discharge confirmed as potential source of failure | 1.5 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 154
Lower | Upper | Bound Description | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | As New | Condition Criteria: Ductor Test Results in % | The joint test result meets the manufacturers recommended value | 1 | 10 | 0.5
0 | 10 | Condition Criteria: Ductor Test Results, Deterioration from new in % | Up to 10% deterioration from the ‘As New’ condition | 1.1 | 10 | 0.5
10 |  | Condition Criteria: Ductor Test Results, Deterioration from new in % | Over 10% deterioration from the ‘As New’ condition | 1.3 | 10 | 0.5
Default | Default | Condition Criteria: Ductor Test Results | No data available | 1 | 10 | 0.5

## 155
Lower | Upper | Bound Description | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | As New | Condition Criteria: IR Test Results in % | The insulation test result meets the manufacturers recommended value | 1 | 10 | 0.5
0 | 10 | Condition Criteria: IR Test Results, Deterioration from new in % | Up to 10% deterioration from the ‘As New’ condition | 1.1 | 10 | 0.5
10 |  | Condition Criteria: IR Test Results, Deterioration from new in % | Over 10% deterioration from the ‘As New’ condition | 1.3 | 10 | 0.5
Default | Default | Condition Criteria: IR Test Results | No data available | 1 | 10 | 0.5

## 156
Lower | Upper | Bound Description | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | As New | Condition Criteria: Oil Test Results in % | The oil or gas test result meets the required European Standard for new oil or gas | 1 | 10 | 0.5
0 | 10 | Condition Criteria: Oil Test Results, Deterioration from new in % | Up to 10% deterioration from the ‘As New’ condition | 1.1 | 10 | 0.5
10 |  | Condition Criteria: Oil Test Results, Deterioration from new in % | Over 10% deterioration from the ‘As New’ condition | 1.3 | 10 | 0.5
Default | Default | Condition Criteria: Oil Test Results | No data available | 1 | 10 | 0.5

## 157
Condition Criteria: Temperature Readings | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Ambient or Below | At or below ambient temperature | 0.9 | 10 | 0.5
Above Ambient | Above ambient temperature | 1 | 10 | 0.5
Substantially Above Ambient | Operating above the manufacturers recommended maximum temperature | 1.1 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 158
Condition Criteria: Trip Timing Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Pass | Trip time within acceptable range for the type of switchgear | 1 | 10 | 0.5
Fail | Trip time slower than acceptable time for the type of switchgear | 1.4 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 159
Condition Criteria: Partial Discharge Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | Low or negligible levels of partial discharge indicating no issues identified (e.g. a green condition using a TEV or <10% of manufacturers recommendation | 1 | 10 | 0.5
Medium | Some moderate levels of partial discharge recorded (e.g. ‘Amber’ result from TEV measuring device or between 10% and 30% of the manufacturers recommendation) | 1.1 | 10 | 0.5
High (Not Confirmed) | High levels of partial discharge indicating possible defect with plant / equipment, requiring further investigation (e.g. ‘Red’ result from TEV measuring device or above manufacturers recommendation) | 1.3 | 10 | 5.5
High (Confirmed) | High partial discharge. Source of partial discharge confirmed as potential source of failure | 1.5 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 160
Lower | Upper | Bound Description | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
0 | 0.15 | Condition Criteria: Oil Acidity (mg KOH/g) | The measure acidity of the oil is in the range indicated | 0.9 | 10 | 0.5
0.15 | 0.3 | Condition Criteria: Oil Acidity (mg KOH/g) | The measure acidity of the oil is in the range indicated | 1 | 10 | 0.5
0.3 | 0.5 | Condition Criteria: Oil Acidity (mg KOH/g) | The measure acidity of the oil is in the range indicated | 1.15 | 10 | 0.5
0.5 |  | Condition Criteria: Oil Acidity (mg KOH/g) | The measure acidity of the oil is in the range indicated | 1.4 | 10 | 0.5
Default | Default | Condition Criteria: Oil Acidity (mg KOH/g) | No data available | 1 | 10 | 0.5

## 161
Condition Criteria: Temperature Reading | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Normal | Normally expected temperature for transformer loading | 1 | 10 | 0.5
Moderately High | Slightly above normally expected temperature for transformer loading | 1.2 | 10 | 0.5
Very High | Significantly above normally expected temperature for transformer loading | 1.4 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 162
Condition Criteria: Partial Discharge Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | Low or negligible levels of partial discharge indicating no issues identified (e.g. a green condition using a TEV or <10% of manufacturers recommendation | 1 | 10 | 0.5
Medium | Some moderate levels of partial discharge recorded (e.g. ‘Amber’ result from TEV measuring device or between 10% and 30% of the manufacturers recommendation) | 1.1 | 10 | 0.5
High (Not Confirmed) | High levels of partial discharge indicating possible defect with plant / equipment, requiring further investigation (e.g. ‘Red’ result from TEV measuring device or above manufacturers recommendation) | 1.3 | 10 | 5.5
High (Confirmed) | High partial Discharge. Source of partial discharge confirmed as potential source of failure | 1.5 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 163
Condition Criteria: Temperature Reading | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Normal | Normally expected temperature for transformer loading | 1 | 10 | 0.5
Moderately High | Slightly above normally expected temperature for transformer loading | 1.2 | 10 | 0.5
Very High | Significantly above normally expected temperature for transformer loading | 1.4 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 164
Condition Criteria: Partial Discharge Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | Low or negligible levels of partial discharge indicating no issues identified (e.g. a green condition using a TEV or <10% of manufacturers recommendation | 1 | 10 | 0.5
Medium | Some moderate levels of partial discharge recorded (e.g. ‘Amber’ result from TEV measuring device or between 10% and 30% of the manufacturers recommendation) | 1.1 | 10 | 0.5
High (Not Confirmed) | High levels of partial discharge indicating possible defect with plant / equipment, requiring further investigation (e.g. ‘Red’ result from TEV measuring device or above manufacturers recommendation) | 1.3 | 10 | 5.5
High (Confirmed) | High partial discharge. Source of partial discharge confirmed as potential source of failure | 1.5 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 165
Condition Criteria: Partial Discharge Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | Low or negligible levels of partial discharge indicating no issues identified (e.g. a green condition using a TEV or <10% of manufacturers recommendation | 1 | 10 | 0.5
Medium | Some moderate levels of partial discharge recorded (e.g. ‘Amber’ result from TEV measuring device or between 10% and 30% of the manufacturers recommendation) | 1.1 | 10 | 0.5
High (Not Confirmed) | High levels of partial discharge indicating possible defect with plant / equipment, requiring further investigation (e.g. ‘Red’ result from TEV measuring device or above manufacturers recommendation) | 1.3 | 10 | 5.5
High (Confirmed) | High partial discharge. Source of partial discharge confirmed as potential source of failure | 1.5 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 166
Condition Criteria: Temperature Reading | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Normal | Normally expected temperature for transformer loading | 1 | 10 | 0.5
Moderately High | Slightly above normally expected temperature for transformer loading | 1.2 | 10 | 0.5
Very High | Significantly above normally expected temperature for transformer loading | 1.4 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 167
Condition Criteria: Partial Discharge Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | Low or negligible levels of partial discharge indicating no issues identified (e.g. a green condition using a TEV or <10% of manufacturers recommendation | 1 | 10 | 0.5
Medium | Some moderate levels of partial discharge recorded (e.g. ‘Amber’ result from TEV measuring device or between 10% and 30% of the manufacturers recommendation) | 1.1 | 10 | 0.5
High (Not Confirmed) | High levels of partial discharge indicating possible defect with plant / equipment, requiring further investigation (e.g. ‘Red’ result from TEV measuring device or above manufacturers recommendation) | 1.3 | 10 | 5.5
High (Confirmed) | High Partial Discharge. Source of partial discharge confirmed as potential source of failure | 1.5 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 168
Condition Criteria: Sheath Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Pass | Satisfactory | 1 | 10 | 0.5
Failed Minor | Failure requiring minor repair | 1.3 | 10 | 0.5
Failed Major | Unacceptable sheath leakage or condition | 1.6 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 169
Condition Criteria: Partial Discharge Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | No unusual activity detected | 1 | 10 | 0.5
Medium | PD detected requiring regular monitoring | 1.15 | 10 | 0.5
High | Intervention required | 1.5 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 170
Lower | Upper | Bound Description | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No historic faults recorded | No historic faults recorded | Condition Criteria: Fault Rate (faults per annum) per km | No recorded faults or failures in the period | 1 | 5.4 | 0.5
0 | 0.01 | Condition Criteria: Fault Rate (faults per annum) per km | The calculated fault rate for the asset in the period | 1.3 | 10 | 0.5
0.01 | 0.1 | Condition Criteria: Fault Rate (faults per annum) per km | The calculated fault rate for the asset in the period | 1.6 | 10 | 5.5
0.1 |  | Condition Criteria: Fault Rate (faults per annum) per km | The calculated fault rate for the asset in the period | 1.8 | 10 | 8
Default | Default | Condition Criteria: Fault Rate (faults per annum) | No data available | 1 | 10 | 0.5

## 172
Condition Criteria: Leakage Rate | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No (or very low) historic leakage recorded | No or negligible levels of leakage | 1 | 10 | 0.5
Low/ moderate | Requires occasional intervention to maintain pressure | 1.3 | 10 | 0.5
High | Requires regular intervention to maintain pressure | 1.8 | 10 | 5.5
Very High | Requires intervention at the point of oil loss | 2 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 174
Condition Criteria: Leakage Rate | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No (or very low) historic leakage recorded | No or negligible levels of leakage | 1 | 10 | 0.5
Low/ moderate | Requires occasional intervention to maintain pressure | 1.3 | 10 | 0.5
High | Requires regular intervention to maintain pressure | 1.8 | 10 | 5.5
Very High | Requires intervention at the point of gas loss | 2 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 175
Condition Criteria: Sheath Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Pass | Satisfactory | 1 | 10 | 0.5
Failed Minor | Failure requiring minor repair | 1.3 | 10 | 0.5
Failed Major | Unacceptable Sheath Leakage or Condition | 1.6 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 176
Condition Criteria: Partial Discharge Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | No unusual activity detected | 1 | 10 | 0.5
Medium | PD detected requiring regular monitoring | 1.15 | 10 | 0.5
High | Intervention required | 1.5 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 177
Lower | Upper | Bound Description | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No historic faults recorded | No historic faults recorded | Condition Criteria: Fault Rate ( faults per annum) per km | No recorded faults or failures in the period | 1 | 5.4 | 0.5
0 | 0.01 | Condition Criteria: Fault Rate ( faults per annum) per km | The calculated fault rate for the asset in the period | 1.3 | 10 | 0.5
0.01 | 0.1 | Condition Criteria: Fault Rate ( faults per annum) per km | The calculated fault rate for the asset in the period | 1.6 | 10 | 5.5
0.1 |  | Condition Criteria: Fault Rate ( faults per annum) per km | The calculated fault rate for the asset in the period | 1.8 | 10 | 8
Default | Default | Condition Criteria: Fault Rate ( faults per annum) | No data available | 1 | 10 | 0.5

## 179
Condition Criteria: Leakage Rate | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No (or very low) historic leakage recorded | No or negligible levels of leakage | 1 | 10 | 0.5
Low/ moderate | Requires occasional intervention to maintain pressure | 1.3 | 10 | 0.5
High | Requires regular intervention to maintain pressure | 1.8 | 10 | 5.5
Very High | Requires intervention at the point of oil loss | 2 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 181
Condition Criteria: Leakage Rate | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No (or very low) historic leakage recorded | No or negligible levels of leakage | 1 | 10 | 0.5
Low/ moderate | Requires occasional intervention to maintain pressure | 1.3 | 10 | 0.5
High | Requires regular intervention to maintain pressure | 1.8 | 10 | 5.5
Very High | Requires intervention at the point of gas loss | 2 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 182
Condition Criteria: Sheath Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Pass | Satisfactory | 1 | 10 | 0.5
Failed Minor | Failure requiring minor repair | 1.3 | 10 | 0.5
Failed Major | Unacceptable sheath leakage or condition | 1.6 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 183
Condition Criteria: Partial Discharge Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | No unusual activity detected | 1 | 10 | 0.5
Medium | PD detected requiring regular monitoring | 1.15 | 10 | 0.5
High | Intervention required | 1.5 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 184
Lower | Upper | Bound Description | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No historic faults recorded | No historic faults recorded | Condition Criteria: Fault Rate (faults per annum) per km | No recorded faults or failures in the period | 1 | 5.4 | 0.5
0 | 0.01 | Condition Criteria: Fault Rate (faults per annum) per km | The calculated fault rate for the asset in the period | 1.3 | 10 | 0.5
0.01 | 0.1 | Condition Criteria: Fault Rate (faults per annum) per km | The calculated fault rate for the asset in the period | 1.6 | 10 | 5.5
0.1 |  | Condition Criteria: Fault Rate (faults per annum) per km | The calculated fault rate for the asset in the period | 1.8 | 10 | 8
Default | Default | Condition Criteria: Fault Rate (faults per annum) | No data available | 1 | 10 | 0.5

## 185
Condition Criteria: Degree of Decay/Deterioration | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
None | Zero measured loss of strength | 0.8 | 5.4 | 0.5
No Significant Decay/Deterioration | Minor loss of strength | 1 | 6.4 | 0.5
High | Significant loss of residual strength, still within acceptable level | 1.4 | 10 | 5.5
Very High | Residual strength below acceptable level | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 186
Condition Criteria: Degree of Decay/Deterioration | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
None | Zero measured loss of strength | 0.8 | 5.4 | 0.5
No Significant Decay/Deterioration | Minor loss of strength | 1 | 6.4 | 0.5
High | Significant loss of residual strength, still within acceptable level | 1.4 | 10 | 5.5
Very High | Residual strength below acceptable level | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 187
Condition Criteria: Degree of Decay/Deterioration | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
None | Zero measured loss of strength | 0.8 | 5.4 | 0.5
No Significant Decay/Deterioration | Minor loss of strength | 1 | 6.4 | 0.5
High | Significant loss of residual strength, still within acceptable level | 1.4 | 10 | 5.5
Very High | Residual strength below acceptable level | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 188
Condition Criteria: Thermal Imaging Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | Ambient plus or minus 100C | 1 | 5.4 | 0.5
Medium | Ambient plus 10 - 250C | 1.1 | 10 | 0.5
High | Ambient plus more than 250C | 1.4 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 189
Condition Criteria: Ductor Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | As commissioned or up to 2.5% variance | 1 | 5.4 | 0.5
Medium | As commissioned or up to 5% variance | 1.1 | 10 | 0.5
High | As commissioned or over 5% variance | 1.4 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 190
Condition Criteria: Thermal Imaging Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | Ambient plus or minus 100C | 1 | 5.4 | 0.5
Medium | Ambient plus 10 - 250C | 1.1 | 10 | 0.5
High | Ambient plus more than 250C | 1.4 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 191
Condition Criteria: Ductor Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | As commissioned or up to 2.5% variance | 1 | 5.4 | 0.5
Medium | As commissioned or up to 5% variance | 1.1 | 10 | 0.5
High | As commissioned or over 5% variance | 1.4 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 192
Condition Criteria: Conductor Sampling Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | No obvious or minor deterioration | 1 | 5.4 | 0.5
Medium/Normal | Wear is consistent with the duty and environment of the circuit | 1.1 | 10 | 0.5
High | Wear indicated that an end of life condition exists | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 193
Condition Criteria: Corrosion Monitoring Survey Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | No obvious or minor deterioration | 1 | 5.4 | 0.5
Medium/Normal | Wear is consistent with the duty and environment of the circuit | 1.1 | 10 | 0.5
High | Wear indicated that an end of life condition exists | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 194
Condition Criteria: Conductor Sampling Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | No obvious or minor deterioration | 1 | 5.4 | 0.5
Medium/Normal | Wear is consistent with the duty and environment of the circuit | 1.1 | 10 | 0.5
High | Wear indicated that an end of life condition exists | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 195
Condition Criteria: Corrosion Monitoring Survey Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | No obvious or minor deterioration | 1 | 5.4 | 0.5
Medium/Normal | Wear is consistent with the duty and environment of the circuit | 1.1 | 10 | 0.5
High | Wear indicated that an end of life condition exists | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 196
Lower | Upper | Bound Description | Moisture Score
-0.01 | 15 | Moisture (ppm) | 0
15 | 25 | Moisture (ppm) | 2
25 | 35 | Moisture (ppm) | 4
35 | 45 | Moisture (ppm) | 8
45 | 10000 | Moisture (ppm) | 10

## 197
Lower | Upper | Bound Description | Acidity Score
-0.01 | 0.1 | Acidity (mg KOH/g) | 0
0.1 | 0.15 | Acidity (mg KOH/g) | 2
0.15 | 0.2 | Acidity (mg KOH/g) | 4
0.2 | 0.3 | Acidity (mg KOH/g) | 8
0.3 | 10000 | Acidity (mg KOH/g) | 10

## 198
Lower | Upper | Bound Description | BD Strength Score
-0.01 | 30 | BD Strength (kV) | 10
30 | 40 | BD Strength (kV) | 4
40 | 50 | BD Strength (kV) | 2
50 | 10000 | BD Strength (kV) | 0

## 199
Lower | Upper | Bound Description | Oil Test Factor
-0.01 | 50 | Oil Condition Score | 0.9
50 | 200 | Oil Condition Score | 1
200 | 500 | Oil Condition Score | 1.05
500 | 1000 | Oil Condition Score | 1.1
1000 | 10000 | Oil Condition Score | 1.2

## 200
Lower | Upper | Bound Description | Oil Test Collar
-0.01 | 50 | Oil Condition Score | 0.5
50 | 200 | Oil Condition Score | 0.5
200 | 500 | Oil Condition Score | 0.5
500 | 1000 | Oil Condition Score | 0.5
1000 | 10000 | Oil Condition Score | 3

## 201
Lower | Upper | Bound Description | Hydrogen Condition State
-0.01 | 20 | Hydrogen (ppm) | 0
20 | 40 | Hydrogen (ppm) | 2
40 | 100 | Hydrogen (ppm) | 4
100 | 200 | Hydrogen (ppm) | 10
200 | 10000 | Hydrogen (ppm) | 16

## 202
Lower | Upper | Bound Description | Methane Condition State
-0.01 | 10 | Methane (ppm) | 0
10 | 20 | Methane (ppm) | 2
20 | 50 | Methane (ppm) | 4
50 | 150 | Methane (ppm) | 10
150 | 10000 | Methane (ppm) | 16

## 203
Lower | Upper | Bound Description | Ethylene Condition State
-0.01 | 10 | Ethylene (ppm) | 0
10 | 20 | Ethylene (ppm) | 2
20 | 50 | Ethylene (ppm) | 4
50 | 150 | Ethylene (ppm) | 10
150 | 10000 | Ethylene (ppm) | 16

## 204
Lower | Upper | Bound Description | Ethane Condition State
-0.01 | 10 | Ethane (ppm) | 0
10 | 20 | Ethane (ppm) | 2
20 | 50 | Ethane (ppm) | 4
50 | 150 | Ethane (ppm) | 10
150 | 10000 | Ethane (ppm) | 16

## 205
Lower | Upper | Bound Description | Acetylene Condition State
-0.01 | 1 | Acetylene (ppm) | 0
1 | 5 | Acetylene (ppm) | 2
5 | 20 | Acetylene (ppm) | 4
20 | 100 | Acetylene (ppm) | 8
100 | 10000 | Acetylene (ppm) | 10

## 206
Lower | Upper | Bound Description | Change Category
-1000 | -5 | % Change | Negative
-5 | 5 | % Change | Neutral
5 | 25 | % Change | Small
25 | 100 | % Change | Significant
100 | 1000 | % Change | Large

## 207
> % Change | DGA Test Factor
Negative | 0.9
Neutral | 1
Small | 1.1
Significant | 1.2
Large | 1.5

## 208
Lower | Upper | Bound Description | FFA Test Factor
-0.01 | 4 | FFA value (ppm) | 1
4 | 5 | FFA value (ppm) | 1.1
5 | 6 | FFA value (ppm) | 1.25
6 | 7 | FFA value (ppm) | 1.4
7 |  | FFA value (ppm) | 1.6

## 209
Lower | Upper | Bound Description | Ageing Reduction Factor
0 | 2 | Current Health Score | 1
2 | 5.5 | Current Health Score | ((Current Health Score - 2)/ 7) + 1
5.5 |  | Current Health Score | 1.5

## 210
Refurbishment Intervention Activity | Health Index Asset Category | Asset Register Category | Input Data Affected By Intervention
Complete replacement of the operating mechanism (ACB) | LV Switchgear | LV Circuit Breaker | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of complete feederway | LV Switchgear | LV Pillar (ID), LV Pillar (OD at Substation) & LV Pillars (OD not at Substation) | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Complete factory refurbishment | HV Switchgear (GM) - Distribution | 6.6/11kV CB (GM) Secondary, 6.6/11kV RMU, 6.6/11kV Switch (GM), 6.6/11kV X-type RMU, 20kV CB (GM) Secondary, 20kV RMU & 20kV Switch (GM) | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Complete Refurbishment (factory or onsite) e.g. strip down & rebuild, replacing all worn parts | HV Switchgear (GM) - Distribution | 6.6/11kV CB (GM) Secondary, 6.6/11kV RMU, 6.6/11kV Switch (GM), 6.6/11kV X-type RMU, 20kV CB (GM) Secondary, 20kV RMU & 20kV Switch (GM) | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Complete replacement of the operating mechanism | HV Switchgear (GM) - Distribution | 6.6/11kV CB (GM) Secondary, 6.6/11kV RMU, 6.6/11kV Switch (GM), 6.6/11kV X-type RMU, 20kV CB (GM) Secondary, 20kV RMU & 20kV Switch (GM) | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of cable boxes | HV Switchgear (GM) - Distribution | 6.6/11kV CB (GM) Secondary, 6.6/11kV RMU, 6.6/11kV Switch (GM), 6.6/11kV X-type RMU, 20kV CB (GM) Secondary, 20kV RMU & 20kV Switch (GM) | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of the moving portion (truck) in withdrawable equipment | HV Switchgear (GM) - Distribution | 6.6/11kV CB (GM) Secondary & 20kV CB (GM) Secondary | i) Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier; and ii) Increase the Expected Life by 20 years
Complete factory refurbishment | HV Switchgear (GM) - Primary | 6.6/11kV CB (GM) Primary & 20kV CB (GM) Primary | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Complete Refurbishment (factory or onsite) e.g. strip down & rebuild, replacing all worn parts | HV Switchgear (GM) - Primary | 6.6/11kV CB (GM) Primary & 20kV CB (GM) Primary | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Complete replacement of the operating mechanism | HV Switchgear (GM) - Primary | 6.6/11kV CB (GM) Primary & 20kV CB (GM) Primary | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of cable boxes | HV Switchgear (GM) - Primary | 6.6/11kV CB (GM) Primary & 20kV CB (GM) Primary | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of the moving portion (truck) in withdrawable equipment | HV Switchgear (GM) - Primary | 6.6/11kV CB (GM) Primary & 20kV CB (GM) Primary | i) Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier; and ii) Increase the Expected Life by 20 years
Complete Refurbishment (factory or onsite) e.g. strip down & rebuild, replacing all worn parts | EHV Switchgear (GM) | 33kV CB (Air Insulated Busbars)(ID) (GM), 33kV CB (Air Insulated Busbars)(OD) (GM), 33kV CB (Gas Insulated Busbars)(ID) (GM), 33kV CB (Gas Insulated Busbars)(OD) (GM), 33kV RMU, 33kV Switch (GM), 66kV CB (Air Insulated Busbars)(ID) (GM), 66kV CB (Air Insulated Busbars)(OD) (GM), 66kV CB (Gas Insulated Busbars)(ID) (GM) & 66kV CB (Gas Insulated Busbars)(OD) (GM) | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Complete replacement of the operating mechanism | EHV Switchgear (GM) | 33kV CB (Air Insulated Busbars)(ID) (GM), 33kV CB (Air Insulated Busbars)(OD) (GM), 33kV CB (Gas Insulated Busbars)(ID) (GM), 33kV CB (Gas Insulated Busbars)(OD) (GM), 33kV RMU, 33kV Switch (GM), 66kV CB (Air Insulated Busbars)(ID) (GM), 66kV CB (Air Insulated Busbars)(OD) (GM), 66kV CB (Gas Insulated Busbars)(ID) (GM) & 66kV CB (Gas Insulated Busbars)(OD) (GM) | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of cable boxes | EHV Switchgear (GM) | 33kV CB (Air Insulated Busbars)(ID) (GM), 33kV CB (Air Insulated Busbars)(OD) (GM), 33kV CB (Gas Insulated Busbars)(ID) (GM), 33kV CB (Gas Insulated Busbars)(OD) (GM), 33kV RMU, 33kV Switch (GM), 66kV CB (Air Insulated Busbars)(ID) (GM), 66kV CB (Air Insulated Busbars)(OD) (GM), 66kV CB (Gas Insulated Busbars)(ID) (GM) & 66kV CB (Gas Insulated Busbars)(OD) (GM) | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of the moving portion (truck) in withdrawable equipment | EHV Switchgear (GM) | 33kV CB (Air Insulated Busbars)(ID) (GM), 33kV CB (Air Insulated Busbars)(OD) (GM) & 33kV CB (Gas Insulated Busbars)(ID) (GM) | i) Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier; and ii) Increase the Expected Life by 20 years
Complete Refurbishment (factory or onsite) e.g. strip down & rebuild, replacing all worn parts | 132kV CBs | 132kV CB (Air Insulated Busbars)(ID) (GM), 132kV CB (Air Insulated Busbars)(OD) (GM), 132kV CB (Gas Insulated Busbars)(ID) (GM) & 132kV CB (Gas Insulated Busbars)(OD) (GM) | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Complete replacement of the operating mechanism | 132kV CBs | 132kV CB (Air Insulated Busbars)(ID) (GM), 132kV CB (Air Insulated Busbars)(OD) (GM), 132kV CB (Gas Insulated Busbars)(ID) (GM) & 132kV CB (Gas Insulated Busbars)(OD) (GM) | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of cable boxes | 132kV CBs | 132kV CB (Air Insulated Busbars)(ID) (GM), 132kV CB (Air Insulated Busbars)(OD) (GM), 132kV CB (Gas Insulated Busbars)(ID) (GM) & 132kV CB (Gas Insulated Busbars)(OD) (GM) | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Complete factory refurbishment | HV Transformer (GM) | 6.6/11kV Transformer (GM) & 20kV Transformer (GM) | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Installation of replacement windings | HV Transformer (GM) | 6.6/11kV Transformer (GM) & 20kV Transformer (GM) | i) Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier; and ii) Revise age to reflect time elapsed since Refurbishment undertaken
On site processing to recondition oil to remove moisture and acidity from windings | HV Transformer (GM) | 6.6/11kV Transformer (GM) & 20kV Transformer (GM) | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of cooling radiators | HV Transformer (GM) | 6.6/11kV Transformer (GM) & 20kV Transformer (GM) | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs and Measured Condition Inputs
Complete factory refurbishment | EHV Transformer | 33kV Transformer (GM) & 66kV Transformer | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Installation of replacement windings | EHV Transformer | 33kV Transformer (GM) & 66kV Transformer | i) Reassess Health Score Modifier for Main Transformer subcomponent by reassessing relevant Observed Condition Inputs, Measured Condition Inputs, Oil Test Modifier, DGA Test Modifier, FFA Test Modifier and Reliability Modifier; and ii) Revise age to reflect time elapsed since Refurbishment undertaken
On site processing to recondition oil to remove moisture and acidity from windings | EHV Transformer | 33kV Transformer (GM) & 66kV Transformer | Reassess Health Score Modifier for Main Transformer subcomponent by reassessing Oil Test Modifier
Replacement of bushings | EHV Transformer | 33kV Transformer (GM) & 66kV Transformer | Reassess Health Score Modifier for Main Transformer subcomponent by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of cooling radiators | EHV Transformer | 33kV Transformer (GM) & 66kV Transformer | Reassess Health Score Modifier for Main Transformer subcomponent by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of gaskets & seals | EHV Transformer | 33kV Transformer (GM) & 66kV Transformer | Reassess Health Score Modifier for Main Transformer subcomponent by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of Tapchangers or full replacement of Tapchanger mechanism | EHV Transformer | 33kV Transformer (GM) & 66kV Transformer | i) Reassess Health Score Modifier for Tapchanger subcomponent by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier; and ii) Where Tapchanger is replaced: revise age of Tapchanger subcomponent, used in the calculation of Initial Health Score, to the age of the new Tapchanger
Complete factory refurbishment | 132kV Transformer | 132kV Transformer | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Installation of replacement windings | 132kV Transformer | 132kV Transformer | i) Reassess Health Score Modifier for Main Transformer subcomponent by reassessing relevant Observed Condition Inputs, Measured Condition Inputs, Oil Test Modifier, DGA Test Modifier, FFA Test Modifier and Reliability Modifier; and ii) Revise age to reflect time elapsed since Refurbishment undertaken
On site processing to recondition oil to remove moisture and acidity from windings | 132kV Transformer | 132kV Transformer | Reassess Health Score Modifier for Main Transformer subcomponent by reassessing Oil Test Modifier
Replacement of bushings | 132kV Transformer | 132kV Transformer | Reassess Health Score Modifier for Main Transformer subcomponent by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of cooling radiators | 132kV Transformer | 132kV Transformer | Reassess Health Score Modifier for Main Transformer subcomponent by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of gaskets & seals | 132kV Transformer | 132kV Transformer | Reassess Health Score Modifier for Main Transformer subcomponent by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of Tapchangers or full replacement of Tapchanger mechanism | 132kV Transformer | 132kV Transformer | i) Reassess Health Score Modifier for Tapchanger subcomponent by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier; and ii) Where Tapchanger is replaced: revise age of Tapchanger subcomponent, used in the calculation of Initial Health Score, to the age of the new Tapchanger
Pole Strengthening (e.g. clamping a steelwork supporting bracket to an existing pole) | LV Poles | LV Poles | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs and Measured Condition Inputs
Small footprint steel masts: Replacement of individual steelwork members | LV Poles | LV Poles | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs and Measured Condition Inputs
Pole Strengthening (e.g. clamping a steelwork supporting bracket to an existing pole) | HV Poles | 6.6/11kV Poles & 20kV Poles | Reassess Health Score Modifier by reassessing Pole Decay/Deterioration Measured Condition Inputs
Small footprint steel masts: Replacement of individual steelwork members | HV Poles | 6.6/11kV Poles & 20kV Poles | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs and Measured Condition Inputs
Pole Strengthening (e.g. clamping a steelwork supporting bracket to an existing pole) | EHV Pole | 33kV Pole & 66kV Pole | Reassess Health Score Modifier by reassessing Pole Decay/Deterioration Measured Condition Inputs
Small footprint steel masts: Replacement of individual steelwork members | EHV Pole | 33kV Pole & 66kV Pole | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs and Measured Condition Inputs
Painting of Tower | EHV Tower | 33kV Tower & 66kV Tower | i) Reassess Health Score Modifier for Tower Paintwork subcomponent by reassessing Paintwork Condition Input; and ii) revise age of Tower Paintwork subcomponent, used in the calculation of Initial Health Score, to the time elapsed since the Tower was most recently painted
Replacement of individual steelwork members | EHV Tower | 33kV Tower & 66kV Tower | Reassess Health Score Modifier for the Tower Steelwork subcomponent by reassessing relevant Observed Condition Inputs
Replacement of Tower foundations | EHV Tower | 33kV Tower & 66kV Tower | Reassess Health Score Modifier for the Tower Foundation subcomponent by reassessing relevant Observed Condition Inputs
Painting of Tower | 132kV Tower | 132kV Tower | i) Reassess Health Score Modifier for Tower Paintwork subcomponent by reassessing Paintwork Condition Input ii) revise age of Tower Paintwork subcomponent, used in the calculation of Initial Health Score, to the time elapsed since the Tower was most recently painted
Replacement of individual steelwork members | 132kV Tower | 132kV Tower | Reassess Health Score Modifier for the Tower Steelwork subcomponent by reassessing relevant Observed Condition Inputs
Replacement of Tower foundations | 132kV Tower | 132kV Tower | Reassess Health Score Modifier for the Tower Foundation subcomponent by reassessing relevant Observed Condition Inputs
Re-engineering (replacement/refurbishment/relocation) of pressurising system equipment with the objective of reducing the normal operating fluid pressure in the cable system | EHV Cable (Gas) | 33kV UG Cable (Gas) & 66kV UG Cable (Gas) | Reassess Health Score Modifier by reassessing relevant Measured Condition Inputs (incl. Leakage Rate Condition Input)
Remaking existing joints and terminations in situ | EHV Cable (Gas) | 33kV UG Cable (Gas) & 66kV UG Cable (Gas) | Reassess Health Score Modifier by reassessing relevant Measured Condition Inputs (incl. Leakage Rate Condition Input)
Replacement of cable joints and terminations (including sealing ends) | EHV Cable (Gas) | 33kV UG Cable (Gas) & 66kV UG Cable (Gas) | Reassess Health Score Modifier by reassessing relevant Measured Condition Inputs (incl. Leakage Rate Condition Input)
Re-engineering (replacement/refurbishment/relocation) of pressurising system equipment with the objective of reducing the normal operating fluid pressure in the cable system | EHV Cable (Oil) | 33kV UG Cable (Oil) & 66kV UG Cable (Oil) | Reassess Health Score Modifier by reassessing relevant Measured Condition Inputs (incl. Leakage Rate Condition Input)
Remaking existing joints and terminations in situ | EHV Cable (Oil) | 33kV UG Cable (Oil) & 66kV UG Cable (Oil) | Reassess Health Score Modifier by reassessing relevant Measured Condition Inputs (incl. Leakage Rate Condition Input)
Replacement of cable joints and terminations (including sealing ends) | EHV Cable (Oil) | 33kV UG Cable (Oil) & 66kV UG Cable (Oil) | Reassess Health Score Modifier by reassessing relevant Measured Condition Inputs (incl. Leakage Rate Condition Input)
Re-engineering (replacement/refurbishment/relocation) of pressurising system equipment with the objective of reducing the normal operating fluid pressure in the cable system | 132kV Cable (Gas) | 132kV UG Cable (Gas) | Reassess Health Score Modifier by reassessing relevant Measured Condition Inputs (incl. Leakage Rate Condition Input)
Remaking existing joints and terminations in situ | 132kV Cable (Gas) | 132kV UG Cable (Gas) | Reassess Health Score Modifier by reassessing relevant Measured Condition Inputs (incl. Leakage Rate Condition Input)
Replacement of cable joints and terminations (including sealing ends) | 132kV Cable (Gas) | 132kV UG Cable (Gas) | Reassess Health Score Modifier by reassessing relevant Measured Condition Inputs (incl. Leakage Rate Condition Input)
Re-engineering (replacement/refurbishment/relocation) of pressurising system equipment with the objective of reducing the normal operating fluid pressure in the cable system | 132kV Cable (Oil) | 132kV UG Cable (Oil) | Reassess Health Score Modifier by reassessing relevant Measured Condition Inputs (incl. Leakage Rate Condition Input)
Remaking existing joints and terminations in situ | 132kV Cable (Oil) | 132kV UG Cable (Oil) | Reassess Health Score Modifier by reassessing relevant Measured Condition Inputs (incl. Leakage Rate Condition Input)
Replacement of cable joints and terminations (including sealing ends) | 132kV Cable (Oil) | 132kV UG Cable (Oil) | Reassess Health Score Modifier by reassessing "relevant Measured Condition Inputs (incl. Leakage Rate" Condition Input)

## 211
Asset Register Category | Relative Proportion Of Failure Modes (as a % of total Functional Failures) - I | Relative Proportion Of Failure Modes (as a % of total Functional Failures) - D | Relative Proportion Of Failure Modes (as a % of total Functional Failures) - C | Likely Cost of Failure - I (GBP) | Likely Cost of Failure - D (GBP) | Likely Cost of Failure - C4 (GBP) | Reference Financial Cose of Failure (GBP)
LV Poles | 20 | 70 | 10 | 136 | 1358 | 1358 | 1113
6.6/11kV Poles | 20 | 70 | 10 | 194 | 1942 | 1942 | 1592
20kV Poles | 20 | 70 | 10 | 233 | 2330 | 2330 | 1910
33kV Pole | 20 | 70 | 10 | 250 | 2503 | 2503 | 2053
66kV Pole | 20 | 70 | 10 | 377 | 3774 | 3774 | 3094
33kV Tower | 80 | 19.95 | 0.05 | 4309 | 10773 | 43094 | 5618
66kV Tower | 80 | 19.95 | 0.05 | 8074 | 20186 | 80742 | 10527
132kV Tower | 80 | 19.95 | 0.05 | 9336 | 23341 | 93364 | 12172
33kV Fittings | 80 | 15 | 5 | 113 | 282 | 1126 | 189
66kV Fittings | 80 | 15 | 5 | 145 | 363 | 1450 | 243
132kV Fittings | 80 | 15 | 5 | 241 | 603 | 2411 | 404
33kV OHL (Tower Line) Conductor | 0 | 85 | 15 | 0 | 12879 | 25758 | 14811
66kV OHL Conductor | 0 | 85 | 15 | 0 | 17082 | 34164 | 19644
132kV OHL (Tower Line) Conductor | 0 | 85 | 15 | 0 | 14772 | 29544 | 16988
HV Sub Cable | 0 | 0 | 100 | 3030 | 7575 | 151492 | 151492
33kV UG Cable (Non Pressurised) | 0 | 0 | 100 | 2634 | 6585 | 26340 | 26340
33kV UG Cable (Oil) | 99 | 0.09 | 0.01 | 100 | 6585 | 26340 | 108
33kV UG Cable (Gas) | 99 | 0.5 | 0.5 | 100 | 6585 | 26340 | 264
66kV UG Cable (Non Pressurised) | 0 | 0 | 100 | 5329 | 13323 | 53291 | 53291
66kV UG Cable (Oil) | 99 | 0.09 | 0.01 | 100 | 13323 | 53291 | 116
66kV UG Cable (Gas) | 99 | 0.5 | 0.5 | 100 | 13323 | 53291 | 432
132kV UG Cable (Non Pressurised) | 0 | 0 | 100 | 9093 | 22733 | 90934 | 90934
132kV UG Cable (Oil) | 99 | 0.09 | 0.01 | 100 | 22733 | 90934 | 129
132kV UG Cable (Gas) | 99 | 0.5 | 0.5 | 100 | 22733 | 90934 | 667
EHV Sub Cable | 0 | 0 | 100 | 4750 | 11875 | 237500 | 237500
132kV Sub Cable | 0 | 0 | 100 | 8000 | 20000 | 400000 | 400000
LV Circuit Breaker | 15 | 25 | 60 | 500 | 1250 | 5000 | 3388
LV Pillar (ID) | 15 | 25 | 60 | 697 | 1741 | 6965 | 4719
LV Pillar (OD at Substation) | 15 | 25 | 60 | 758 | 1895 | 7581 | 5136
LV UGB & LV Pillars (OD not at Substation) | 15 | 25 | 60 | 421 | 1053 | 4213 | 2854
LV Board (WM) | 15 | 25 | 60 | 962 | 2406 | 9624 | 6520
LV Board (X-type Network) (WM) | 15 | 25 | 60 | 1136 | 2839 | 11357 | 7694
6.6/11kV CB (GM) Primary | 45 | 50 | 5 | 2870 | 7176 | 28705 | 6315
6.6/11kV CB (GM) Secondary | 15 | 25 | 60 | 855 | 2137 | 8550 | 5792
6.6/11kV Switch (GM) | 15 | 25 | 60 | 647 | 1618 | 6471 | 4384
6.6/11kV RMU | 15 | 25 | 60 | 1209 | 3022 | 12089 | 8190
6.6/11kV X-type RMU | 15 | 25 | 60 | 1636 | 4090 | 16358 | 11083
20kV CB (GM) Primary | 45 | 50 | 5 | 3596 | 8990 | 35961 | 7911
20kV CB (GM) Secondary | 15 | 25 | 60 | 886 | 2216 | 8863 | 6005
20kV Switch (GM) | 15 | 25 | 60 | 750 | 1875 | 7500 | 5081
20kV RMU | 15 | 25 | 60 | 1231 | 3079 | 12315 | 8343
33kV CB (Air Insulated Busbars)(ID) (GM) | 45 | 50 | 5 | 5491 | 13728 | 54914 | 12081
33kV CB (Air Insulated Busbars)(OD) (GM) | 45 | 50 | 5 | 6761 | 16903 | 67610 | 14874
33kV CB (Gas Insulated Busbars)(ID) (GM) | 45 | 50 | 5 | 8318 | 20794 | 83176 | 18299
33kV CB (Gas Insulated Busbars)(OD) (GM) | 45 | 50 | 5 | 8318 | 20794 | 83176 | 18299
33kV Switch (GM) | 45 | 50 | 5 | 3881 | 9702 | 38807 | 8537
33kV RMU | 45 | 50 | 5 | 9590 | 23976 | 95903 | 21099
66kV CB (Air Insulated Busbars)(ID) (GM) | 45 | 50 | 5 | 10946 | 27365 | 109459 | 24081
66kV CB (Air Insulated Busbars)(OD) (GM) | 45 | 50 | 5 | 17500 | 43750 | 175000 | 38500
66kV CB (Gas Insulated Busbars)(ID) (GM) | 45 | 50 | 5 | 19741 | 49353 | 197413 | 43431
66kV CB (Gas Insulated Busbars)(OD) (GM) | 45 | 50 | 5 | 19741 | 49353 | 197413 | 43431
132kV CB (Air Insulated Busbars)(ID) (GM) | 45 | 50 | 5 | 30682 | 76705 | 306821 | 67501
132kV CB (Air Insulated Busbars)(OD) (GM) | 45 | 50 | 5 | 14446 | 36115 | 144461 | 31781
132kV CB (Gas Insulated Busbars)(ID) (GM) | 45 | 50 | 5 | 63902 | 159755 | 639021 | 140585
132kV CB (Gas Insulated Busbars)(OD) (GM) | 45 | 50 | 5 | 63902 | 159755 | 639021 | 140585
6.6/11kV Transformer (GM) | 15 | 25 | 60 | 1142 | 2856 | 11422 | 7739
20kV Transformer (GM) | 15 | 25 | 60 | 1301 | 3251 | 13005 | 8811
33kV Transformer (GM) | 45 | 50 | 5 | 33182 | 82954 | 331816 | 73000
66kV Transformer | 45 | 50 | 5 | 51001 | 127504 | 510015 | 112203
132kV Transformer | 45 | 50 | 5 | 99514 | 248786 | 995144 | 218932

## 212
Asset Register Category | Type Financial Factor Criteria | Lower | Upper | Bound Description | Type Financial Factor
LV Poles | Pole (excluding terminal poles) |  |  |  | 1
LV Poles | Pole (terminal poles) |  |  |  | 1.2
LV Poles | Steel Poles |  |  |  | 2
LV Board (WM) | Non Asbestos clad |  |  |  | 1
LV Board (WM) | Asbestos clad |  |  |  | 2
LV Board (X-type Network) (WM) | Non Asbestos clad |  |  |  | 1
LV Board (X-type Network) (WM) | Asbestos clad |  |  |  | 2
6.6/11kV Poles | Pole (supporting conductor only) |  |  |  | 1
6.6/11kV Poles | Pole (supporting plant or equipment) |  |  |  | 1.7
6.6/11kV Poles | Small footprint steel masts |  |  |  | 2
20kV Poles | Pole (supporting conductor only) |  |  |  | 1
20kV Poles | Pole (supporting plant or equipment) |  |  |  | 1.7
20kV Poles | Small footprint steel masts |  |  |  | 2
33kV Pole | Pole (supporting conductor only) |  |  |  | 1
33kV Pole | Pole (supporting plant or equipment) |  |  |  | 1.7
33kV Pole | Small footprint steel masts |  |  |  | 2
66kV Pole | Pole (supporting conductor only) |  |  |  | 1
66kV Pole | Pole (supporting plant or equipment) |  |  |  | 1.7
66kV Pole | Small footprint steel masts |  |  |  | 2
33kV Tower | Suspension |  |  |  | 1
33kV Tower | Tension |  |  |  | 1.05
33kV Tower | Terminal |  |  |  | 1.1
66kV Tower | Suspension |  |  |  | 1
66kV Tower | Tension |  |  |  | 1.05
66kV Tower | Terminal |  |  |  | 1.1
33kV Fittings | Suspension |  |  |  | 1
33kV Fittings | Tension |  |  |  | 2
66kV Fittings | Suspension |  |  |  | 1
66kV Fittings | Tension |  |  |  | 2
132kV Fittings | Suspension |  |  |  | 1
132kV Fittings | Tension |  |  |  | 2
132kV Tower | Suspension |  |  |  | 1
132kV Tower | Tension |  |  |  | 1.05
132kV Tower | Terminal |  |  |  | 1.1
6.6/11kV Transformer (GM) |  | 0 | 500 | kVA | 0.85
6.6/11kV Transformer (GM) |  | 500 | 750 | kVA | 1
6.6/11kV Transformer (GM) |  | 750 |  | kVA | 1.15
20kV Transformer (GM) |  | 0 | 500 | kVA | 0.85
20kV Transformer (GM) |  | 500 | 750 | kVA | 1
20kV Transformer (GM) |  | 750 |  | kVA | 1.15
33kV Transformer (GM) | 33/20kV, CMR equivalent | 0 | 10 | MVA, CMR equivalent | 1
33kV Transformer (GM) | 33/20kV, CMR equivalent | 10 | 20 | MVA, CMR equivalent | 1.1
33kV Transformer (GM) | 33/20kV, CMR equivalent | 20 |  | MVA, CMR equivalent | 1.25
33kV Transformer (GM) | 33/11 or 6.6kV, CMR equivalent | 0 | 10 | MVA, CMR equivalent | 0.9
33kV Transformer (GM) | 33/11 or 6.6kV, CMR equivalent | 10 | 20 | MVA, CMR equivalent | 1
33kV Transformer (GM) | 33/11 or 6.6kV, CMR equivalent | 20 |  | MVA, CMR equivalent | 1.1
66kV Transformer (GM) | 66/20kV, CMR equivalent | 0 | 10 | MVA, CMR equivalent | 1
66kV Transformer (GM) | 66/20kV, CMR equivalent | 10 | 20 | MVA, CMR equivalent | 1.1
66kV Transformer (GM) | 66/20kV, CMR equivalent | 20 |  | MVA, CMR equivalent | 1.25
66kV Transformer (GM) | 66/11 or 6.6kV, CMR equivalent | 0 | 10 | MVA, CMR equivalent | 0.9
66kV Transformer (GM) | 66/11 or 6.6kV, CMR equivalent | 10 | 20 | MVA, CMR equivalent | 1
66kV Transformer (GM) | 66/11 or 6.6kV, CMR equivalent | 20 |  | MVA, CMR equivalent | 1.1
132kV Transformer (GM) | 132/66kV | 0 | 60 | MVA | 1.05
132kV Transformer (GM) | 132/66kV | 60 |  | MVA | 1.15
132kV Transformer (GM) | 132/33kV | 0 | 60 | MVA | 0.9
132kV Transformer (GM) | 132/33kV | 60 |  | MVA | 1
66kV Transformer (GM) | 66/33kV |  |  |  | 1.1
66kV Transformer (GM) | 66/11/11kV |  |  |  | 1.1
132kV Transformer (GM) | 132/11/11kV |  |  |  | 1.1
132kV Transformer (GM) | 132/11kV |  |  |  | 0.85
132kV Transformer (GM) | 132/20kV |  |  |  | 0.95
132kV Transformer (GM) | 132/20/20kV |  |  |  | 1.1

## 213
Asset Category | Access Factor: Type A Criteria - Normal Access ( & Default Value) | Access Factor: Type B Criteria - Major Crossing (e.g. associated span crosses railway line, major road, large waterway etc.)
LV OHL Support | 1 | 3
HV OHL Support - Poles | 1 | 3
EHV OHL Support - Poles | 1 | 3
EHV OHL Support - Towers | 1 | 1.5
EHV OHL Fittings (Tower Lines) | 1 | 2
EHV OHL Conductors (Tower Lines) | 1 | 2
132kV OHL Support - Tower | 1 | 1.5
132kV OHL Fittings (Tower Lines) | 1 | 2
132kV OHL Conductors (Tower Lines) | 1 | 2

## 214
Asset Category | Access Factor: Type A Criteria - Normal Access ( & Default Value) | Access Factor: Type B Criteria - Constrained Access or Confined Working Space | Access Factor: Type C Criteria - Underground substation
LV Switchgear | 1 | 1.25 | 1.7
HV Transformer (GM) | 1 | 1.25 | 2
HV Switchgear (GM) - Distribution | 1 | 1.25 | 1.7
HV Switchgear (GM) - Primary | 1 | 1.15 | 1.3
EHV Switchgear (GM) | 1 | 1.1 | 1.25
132kV CBs | 1 | 1.1 | 1.2
EHV Transformer | 1 | 1.1 | 1.35
132kV Transformer | 1 | 1.1 | 1.25

## 215
Asset Register Category | PROBABILITY OF EVENT PER ASSET FAILURE: Lost Time Accident | PROBABILITY OF EVENT PER ASSET FAILURE: Death or Serious Injury to public | PROBABILITY OF EVENT PER ASSET FAILURE: Death or Serious Injury to staff
LV Poles | 0.000816 | 3.264e-05 | 1.632e-05
6.6/11kV Poles | 0.000272 | 1.088e-05 | 5.44e-06
20kV Poles | 0.000272 | 1.088e-05 | 5.44e-06
33kV Pole | 0.000272 | 1.088e-05 | 5.44e-06
66kV Pole | 0.000272 | 1.088e-05 | 5.44e-06
33kV Tower | 0.000136 | 5.44e-06 | 2.72e-05
66kV Tower | 0.000136 | 5.44e-06 | 2.72e-05
132kV Tower | 0.000136 | 5.44e-06 | 2.72e-05
33kV Fittings | 0.000544 | 2.176e-05 | 0.0001088
66kV Fittings | 0.000544 | 2.176e-05 | 0.0001088
132kV Fittings | 0.000544 | 2.176e-05 | 0.0001088
33kV OHL (Tower Line) Conductor | 0.000544 | 2.176e-05 | 0.0001088
66kV OHL Conductor | 0.000544 | 2.176e-05 | 0.0001088
132kV OHL (Tower Line) Conductor | 0.000544 | 2.176e-05 | 0.0001088
HV Sub Cable | 7.5e-07 | 7.5e-08 | 7.5e-08
33kV UG Cable (Non Pressurised) | 7.5e-07 | 7.5e-08 | 7.5e-08
33kV UG Cable (Oil) | 7.5e-07 | 7.5e-08 | 7.5e-08
33kV UG Cable (Gas) | 7.5e-07 | 7.5e-08 | 7.5e-08
66kV UG Cable (Non Pressurised) | 7.5e-07 | 7.5e-08 | 7.5e-08
66kV UG Cable (Oil) | 7.5e-07 | 7.5e-08 | 7.5e-08
66kV UG Cable (Gas) | 7.5e-07 | 7.5e-08 | 7.5e-08
132kV UG Cable (Non Pressurised) | 7.5e-07 | 7.5e-08 | 7.5e-08
132kV UG Cable (Oil) | 7.5e-07 | 7.5e-08 | 7.5e-08
132kV UG Cable (Gas) | 7.5e-07 | 7.5e-08 | 7.5e-08
EHV Sub Cable | 7.5e-07 | 7.5e-08 | 7.5e-08
132kV Sub Cable | 7.5e-07 | 7.5e-08 | 7.5e-08
LV Circuit Breaker | 4.916e-05 | 0.00043441 | 0.00037031
LV Pillar (ID) | 4.916e-05 | 0.00043441 | 0.00037031
LV Pillar (OD at Substation) | 4.916e-05 | 0.00043441 | 0.00037031
LV UGB & LV Pillars (OD not at Substation) | 5.193e-05 | 0.00045891 | 0.0003912
LV Board (WM) | 4.916e-05 | 0.00043441 | 0.00037031
LV Board (X-type Network) (WM) | 4.916e-05 | 0.00043441 | 0.00037031
6.6/11kV CB (GM) Primary | 0.00026027 | 0.000115 | 0.0019606
6.6/11kV CB (GM) Secondary | 2.6027e-05 | 0.00023 | 0.00019606
6.6/11kV Switch (GM) | 2.6027e-05 | 0.00023 | 0.00019606
6.6/11kV RMU | 2.6027e-05 | 0.00023 | 0.00019606
6.6/11kV X-type RMU | 2.6027e-05 | 0.00023 | 0.00019606
20kV CB (GM) Primary | 0.00026027 | 0.000115 | 0.0019606
20kV CB (GM) Secondary | 2.6027e-05 | 0.00023 | 0.00019606
20kV Switch (GM) | 2.6027e-05 | 0.00023 | 0.00019606
20kV RMU | 2.6027e-05 | 0.00023 | 0.00019606
33kV CB (Air Insulated Busbars)(ID) (GM) | 0.00026027 | 0.000115 | 0.0019606
33kV CB (Air Insulated Busbars)(OD) (GM) | 0.00026027 | 0.000115 | 0.0019606
33kV CB (Gas Insulated Busbars)(ID) (GM) | 0.00026027 | 0.000115 | 0.0019606
33kV CB (Gas Insulated Busbars)(OD) (GM) | 0.00026027 | 0.000115 | 0.0019606
33kV Switch (GM) | 0.00026027 | 0.000115 | 0.0019606
33kV RMU | 0.00026027 | 0.000115 | 0.0019606
66kV CB (Air Insulated Busbars)(ID) (GM) | 0.00026027 | 0.000115 | 0.0019606
66kV CB (Air Insulated Busbars)(OD) (GM) | 0.00026027 | 0.000115 | 0.0019606
66kV CB (Gas Insulated Busbars)(ID) (GM) | 0.00026027 | 0.000115 | 0.0019606
66kV CB (Gas Insulated Busbars)(OD) (GM) | 0.00026027 | 0.000115 | 0.0019606
132kV CB (Air Insulated Busbars)(ID) (GM) | 0.00041644 | 5.75e-05 | 0.003137
132kV CB (Air Insulated Busbars)(OD) (GM) | 0.00041644 | 5.75e-05 | 0.003137
132kV CB (Gas Insulated Busbars)(ID) (GM) | 0.00041644 | 5.75e-05 | 0.003137
132kV CB (Gas Insulated Busbars)(OD) (GM) | 0.00041644 | 5.75e-05 | 0.003137
6.6/11kV Transformer (GM) | 2.6027e-05 | 0.00023 | 0.00019606
20kV Transformer (GM) | 2.6027e-05 | 0.00023 | 0.00019606
33kV Transformer (GM) | 0.00026027 | 0.000115 | 0.0019606
66kV Transformer | 0.00026027 | 0.000115 | 0.0019606
132kV Transformer | 0.00041644 | 5.75e-05 | 0.003137

## 216
Reference safety cost | Value (GBP)
Lost Time Accident | 9000
Death or Serious Injury to public | 1600000
Death or Serious Injury to staff | 1600000

## 217
Reference safety cost | Value
Disproportion Factor | 6.25

## 218
Safety Consequence Factor - Switchgear, Transformers & Overhead Lines | Safety Consequence Factor - Switchgear, Transformers & Overhead Lines | TYPE RISK RATING: Low | TYPE RISK RATING: Medium (Default) | TYPE RISK RATING: High
LOCATION RISK RATING | Low | 0.7 | 0.9 | 1.2
LOCATION RISK RATING | Medium (Default) | 0.9 | 1 | 1.4
LOCATION RISK RATING | High | 1.2 | 1.4 | 1.6

## 219
CABLES | SAFETY CONSEQUENCE FACTOR
Buried | 1
Exposed (e.g. cable structure) | 2

## 220
Asset Category | Average volume of oil lost per failure (litres) - I | Average volume of oil lost per failure (litres) - D | Average volume of oil lost per failure (litres) - C | Average volume of SF6 lost per failure (kg) - I | Average volume of SF6 lost per failure (kg) - D | Average volume of SF6 lost per failure (kg) - C | Average probability that failure results in a fire - I | Average probability that failure results in a fire - D | Average probability that failure results in a fire - C | Average quantity of waste per failure (t) - I | Average quantity of waste per failure (t) - D | Average quantity of waste per failure (t) - C | Failures as % of All Failures - I | Failures as % of All Failures - D | Failures as % of All Failures - C | Reference Environmental Consequence (GBP)
LV OHL Support | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0005 | 0.5 | 0.5 | 0.5 | 49 | 49 | 2 | 75
HV OHL Support - Poles | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0005 | 0.5 | 0.5 | 0.5 | 49 | 49 | 2 | 75
EHV OHL Support - Poles | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0005 | 0.5 | 0.5 | 0.5 | 49 | 49 | 2 | 75
EHV UG Cable (Gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.2 | 0.2 | 10 | 45 | 54 | 1 | 45
132kV UG Cable (Gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.3 | 0.3 | 15 | 45 | 54 | 1 | 67
EHV UG Cable (Oil) | 120 | 120 | 1200 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.8 | 0.8 | 40 | 45 | 54 | 1 | 4898
132kV UG Cable (Oil) | 150 | 150 | 1500 | 0 | 0 | 0 | 0 | 0 | 0.001 | 1.2 | 1.2 | 60 | 45 | 54 | 1 | 6167
LV Switchgear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0002 | 0.005 | 0.01 | 0.1 | 0.25 | 50 | 30 | 20 | 18
LV UGB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0002 | 0.05 | 0.01 | 0.1 | 0.5 | 50 | 30 | 20 | 71
HV Switchgear (GM) - Primary | 10 | 50 | 150 | 0.2 | 0.4 | 0.7 | 0 | 0.0005 | 0.01 | 0.1 | 0.2 | 0.5 | 65 | 30 | 5 | 1141
HV Switchgear (GM) - Distribution | 10 | 50 | 150 | 0.1 | 0.2 | 0.5 | 0 | 0.0005 | 0.01 | 0.1 | 0.2 | 0.5 | 65 | 30 | 5 | 1108
EHV Switchgear (GM) | 25 | 125 | 250 | 0.2 | 0.5 | 1 | 0 | 0.0005 | 0.01 | 0.2 | 0.5 | 2 | 70 | 20 | 10 | 2589
132kV CBs | 50 | 250 | 1000 | 0.5 | 1 | 2 | 0 | 0.0005 | 0.01 | 0.3 | 2 | 10 | 70 | 20 | 10 | 7102
HV Transformer (GM) | 20 | 100 | 300 | 0 | 0 | 0 | 0.0002 | 0.002 | 0.02 | 1 | 2 | 5 | 50 | 40 | 10 | 3171
EHV Transformer | 50 | 250 | 2500 | 0 | 0 | 0 | 0.0002 | 0.002 | 0.02 | 0.2 | 3 | 30 | 50 | 40 | 10 | 14190
132kV Transformer | 100 | 500 | 5000 | 0 | 0 | 0 | 0.0002 | 0.002 | 0.02 | 0.5 | 10 | 100 | 50 | 40 | 10 | 29212
EHV UG Cable (Non Pressurised) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 4 | 0 | 0 | 100 | 605
132kV UG Cable (Non Pressurised) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 6 | 0 | 0 | 100 | 905
Submarine Cables | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 100 | 3000
EHV OHL Support - Towers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 1 | 0 | 0 | 100 | 155
132kV OHL Support - Tower | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 1 | 0 | 0 | 100 | 155
EHV OHL Fittings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0.5 | 0 | 0 | 100 | 80
132kV OHL Fittings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0.5 | 0 | 0 | 100 | 80
EHV OHL Conductor (Tower Lines) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0.5 | 0 | 0 | 100 | 80
132kV OHL Conductor (Tower Lines) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0.5 | 0 | 0 | 100 | 80

## 221
Type environment factor | Oil | SF6 | Neither | Default
HV Switchgear (GM) - Primary | 0.94 | 0.08 | 0.02 | 0.94
HV Switchgear (GM) - Distribution | 0.97 | 0.05 | 0.02 | 0.97
EHV Switchgear (GM) | 0.97 | 0.06 | 0.03 | 0.97
132kV CBs | 0.97 | 0.06 | 0.03 | 0.97

## 222
Asset Register Category | Size | Lower | Upper | Bound Description | Size Environmental Factor
6.6/11kV Transformer (GM) |  | 0 | 500 | kVA, Environmental Factor Criteria | 0.6
6.6/11kV Transformer (GM) |  | 500 | 750 | kVA, Environmental Factor Criteria | 1
6.6/11kV Transformer (GM) |  | 750 |  | kVA, Environmental Factor Criteria | 1
20kV Transformer (GM) |  | 0 | 500 | kVA, Environmental Factor Criteria | 0.6
20kV Transformer (GM) |  | 500 | 750 | kVA, Environmental Factor Criteria | 1
20kV Transformer (GM) |  | 750 |  | kVA, Environmental Factor Criteria | 1
33kV Transformer (GM) | 33/20kV | 0 | 10 | MVA, CMR equivalent, Environmental Factor Criteria | 0.7
33kV Transformer (GM) | 33/20kV | 10 | 20 | MVA, CMR equivalent, Environmental Factor Criteria | 1
33kV Transformer (GM) | 33/20kV | 20 |  | MVA, CMR equivalent, Environmental Factor Criteria | 1.6
33kV Transformer (GM) | 33/11 or 6.6kV | 0 | 10 | MVA, CMR equivalent, Environmental Factor Criteria | 0.7
33kV Transformer (GM) | 33/11 or 6.6kV | 10 | 20 | MVA, CMR equivalent, Environmental Factor Criteria | 1
33kV Transformer (GM) | 33/11 or 6.6kV | 20 |  | MVA, CMR equivalent, Environmental Factor Criteria | 1.6
66kV Transformer (GM) | 66/20kV | 0 | 10 | MVA, CMR equivalent, Environmental Factor Criteria | 0.7
66kV Transformer (GM) |  | 10 | 20 | MVA, CMR equivalent, Environmental Factor Criteria | 1
66kV Transformer (GM) |  | 20 |  | MVA, CMR equivalent, Environmental Factor Criteria | 1.6
66kV Transformer (GM) | 66/11 or 6.6kV | 0 | 10 | MVA, CMR equivalent, Environmental Factor Criteria | 0.7
66kV Transformer (GM) | 66/11 or 6.6kV | 10 | 20 | MVA, CMR equivalent, Environmental Factor Criteria | 1
66kV Transformer (GM) | 66/11 or 6.6kV | 20 |  | MVA, CMR equivalent, Environmental Factor Criteria | 1.6
132kV Transformer (GM) | 132/33kV | 0 | 60 | MVA, Environmental Factor Criteria | 0.8
132kV Transformer (GM) | 132/33kV | 60 |  | MVA, Environmental Factor Criteria | 1
132kV Transformer (GM) | 132/33kV | 0 | 60 | MVA, Environmental Factor Criteria | 0.8
132kV Transformer (GM) | 132/33kV | 60 |  | MVA, Environmental Factor Criteria | 1
66kV Transformer (GM) | 66/33kV |  |  |  | 1.2
66kV Transformer (GM) | 66/11/11kV |  |  |  | 1.2
132kV Transformer (GM) | 132/11/11kV |  |  |  | 0.8
132kV Transformer (GM) | 132/11kV |  |  |  | 0.7
132kV Transformer (GM) | 132/20kV |  |  |  | 0.7
132kV Transformer (GM) | 132/20/20kV |  |  |  | 0.8

## 223
Asset Register Category | Proximity Factor: Not Close to Water Course (>120m) or No Oil | Proximity Factor: Moderately Close to Water Course (between 80m and 120m) | Proximity Factor: Close to Water Course (between 40m and 80m) | Proximity Factor: Very Close to Water Course (<40m) | Bunding Factor: Bunded | Bunding Factor: Not bunded
EHV UG Cable (Oil) | 0.8 | 1 | 1.5 | 2.5 | 0.5 | 1
132kV UG Cable (Oil) | 0.8 | 1 | 1.5 | 2.5 | 0.5 | 1
HV Switchgear (GM) - Primary | 0.8 | 1 | 1.5 | 2.5 | 0.5 | 1
HV Switchgear (GM) - Distribution | 0.8 | 1 | 1.5 | 2.5 | 0.5 | 1
EHV Switchgear (GM) | 0.8 | 1 | 1.5 | 2.5 | 0.5 | 1
132kV CBs | 0.8 | 1 | 1.5 | 2.5 | 0.5 | 1
HV Transformer (GM) | 0.8 | 1 | 1.5 | 2.5 | 0.5 | 1
EHV Transformer | 0.8 | 1 | 1.5 | 2.5 | 0.5 | 1
132kV Transformer | 0.8 | 1 | 1.5 | 2.5 | 0.5 | 1

## 224
Parameter | GBP (at 2012/13 prices)
Cost of CML | 0.38
Cost of CI | 15.44

## 225
Asset Category | Reference Number of Connected Customers | Proportion of connected customers restored through immediate (< 3min) switching (%) | Proportion of customers restored After manual switching (%) | Manual switching time (hours) | Typical repair time (hours) | Proportion of failures that result in interruption to supply (%) | Reference Network Performance Cost (GBP)
LV OHL Support | 80 | 0 | 0 | 1 | 5 | 10 | 1218
HV OHL Support - Poles | 800 | 60 | 94 | 0.5 | 4 | 10 | 1297
HV Transformer (GM) | 200 | 0 | 85 | 0.5 | 4 | 60 | 4862
HV Switchgear (GM) - Distribution | 800 | 60 | 94 | 0.5 | 4 | 60 | 7780
HV Switchgear (GM) - Primary | 1000 | 60 | 94 | 0.5 | 4 | 60 | 9725
LV Circuit Breaker | 200 | 0 | 85 | 1 | 7 | 100 | 12436
LV Pillar | 200 | 25 | 89 | 1 | 7 | 100 | 9247
LV UGB | 80 | 25 | 89 | 1 | 7 | 100 | 3699
LV Board (WM) | 200 | 25 | 89 | 1 | 7 | 100 | 9247
HV Sub Cable | 800 | 40 | 60 | 2 | 18 | 100 | 160627

## 226
Lower | Upper | Bound Description | No. of Customers to be used in the derivation of Customer Factor
0 | 50 | Maximum Demand on Asset / Total Number of Customers fed by the Asset (kVA per Customer) Higher Bound | 1 x actual number of customers fed by the asset
50 | 100 | Maximum Demand on Asset / Total Number of Customers fed by the Asset (kVA per Customer) Higher Bound | 25 x actual number of customers fed by the asset
100 | 500 | Maximum Demand on Asset / Total Number of Customers fed by the Asset (kVA per Customer) Higher Bound | 100 x actual number of customers fed by the asset
500 | 1000 | Maximum Demand on Asset / Total Number of Customers fed by the Asset (kVA per Customer) Higher Bound | 250 x actual number of customers fed by the asset
1000 | 2000 | Maximum Demand on Asset / Total Number of Customers fed by the Asset (kVA per Customer) Higher Bound | 500 x actual number of customers fed by the asset
2000 |  | Maximum Demand on Asset / Total Number of Customers fed by the Asset (kVA per Customer) Higher Bound | 1000 x actual number of customers fed by the asset

## 227
Asset Category | Maximum Demand Used To Derive Reference Cost (MVA) | Load at Risk (MVA) as % of Maximum Demand - During T1 period (%) | Load at Risk (MVA) as % of Maximum Demand - During T2 period (%) | Load at Risk (MVA) as % of Maximum Demand - During T3 period (%) | Time (hours) - T1 | Time (hours) - T2 | Time (hours) - T3 | Probability of a coincident fault per hr (%) | Proportion of failures that result in an unplanned outage (%) | Reference Cost For Assets In Secure Networks (GBP)
33kV Pole | 9 | 100 | 100 | 80 | 0 | 3 | 5 | 0.05 | 10 | 57
66kV Pole | 18 | 100 | 100 | 80 | 0 | 3 | 5 | 0.05 | 10 | 114
33kV Tower | 9 | 100 | 100 | 80 | 0 | 3 | 24 | 0.05 | 20 | 362
66kV Tower | 18 | 100 | 100 | 80 | 0 | 3 | 36 | 0.05 | 20 | 1039
132kV Tower | 36 | 100 | 100 | 80 | 0 | 3 | 36 | 0.05 | 20 | 2077
33kV Fittings | 9 | 100 | 100 | 80 | 0 | 3 | 9 | 0.05 | 20 | 167
66kV Fittings | 18 | 100 | 100 | 80 | 0 | 3 | 9 | 0.05 | 20 | 333
132kV Fittings | 36 | 100 | 100 | 80 | 0 | 3 | 9 | 0.05 | 20 | 666
33kV OHL (Tower Line) Conductor | 9 | 100 | 100 | 80 | 0 | 3 | 9 | 0.05 | 100 | 833
66kV OHL Conductor | 18 | 100 | 100 | 80 | 0 | 3 | 9 | 0.05 | 100 | 1666
132kV OHL (Tower Line) Conductor | 36 | 100 | 100 | 80 | 0 | 3 | 9 | 0.05 | 100 | 3331
33kV UG Cable (Non Pressurised) | 10.5 | 100 | 100 | 80 | 0 | 3 | 30 | 0.05 | 100 | 2572
33kV UG Cable (Oil) | 10.5 | 100 | 100 | 80 | 0 | 3 | 30 | 0.05 | 0.1 | 3
33kV UG Cable (Gas) | 10.5 | 100 | 100 | 80 | 0 | 3 | 30 | 0.05 | 1 | 26
66kV UG Cable (Non Pressurised) | 21 | 100 | 100 | 80 | 0 | 3 | 30 | 0.05 | 100 | 5144
66kV UG Cable (Oil) | 21 | 100 | 100 | 80 | 0 | 3 | 30 | 0.05 | 0.1 | 5
66kV UG Cable (Gas) | 21 | 100 | 100 | 80 | 0 | 3 | 30 | 0.05 | 1 | 51
132kV UG Cable (Non Pressurised) | 42 | 100 | 100 | 80 | 0 | 3 | 30 | 0.05 | 100 | 10287
132kV UG Cable (Oil) | 42 | 100 | 100 | 80 | 0 | 3 | 30 | 0.05 | 0.1 | 10
132kV UG Cable (Gas) | 42 | 100 | 100 | 80 | 0 | 3 | 30 | 0.05 | 1 | 103
EHV Sub Cable | 10.5 | 100 | 100 | 80 | 0 | 3 | 30 | 0.05 | 100 | 2572
132kV Sub Cable | 42 | 100 | 100 | 80 | 0 | 3 | 30 | 0.05 | 100 | 10287
33kV CB (Air Insulated Busbars)(ID) (GM) | 30 | 100 | 100 | 80 | 0 | 2 | 200 | 0.05 | 55 | 24248
33kV CB (Air Insulated Busbars)(OD) (GM) | 30 | 100 | 100 | 80 | 0 | 2 | 100 | 0.05 | 55 | 12274
33kV CB (Gas Insulated Busbars)(ID) (GM) | 30 | 100 | 100 | 80 | 0 | 2 | 200 | 0.05 | 55 | 24248
33kV CB (Gas Insulated Busbars)(OD) (GM) | 30 | 100 | 100 | 80 | 0 | 2 | 100 | 0.05 | 55 | 12274
33kV Switch (GM) | 30 | 100 | 100 | 80 | 0 | 2 | 100 | 0.05 | 55 | 12274
33kV RMU | 30 | 100 | 100 | 80 | 0 | 2 | 100 | 0.05 | 55 | 12274
66kV CB (Air Insulated Busbars)(ID) (GM) | 30 | 100 | 100 | 80 | 0 | 2 | 200 | 0.05 | 55 | 24248
66kV CB (Air Insulated Busbars)(OD) (GM) | 30 | 100 | 100 | 80 | 0 | 2 | 100 | 0.05 | 55 | 12274
66kV CB (Gas Insulated Busbars)(ID) (GM) | 30 | 100 | 100 | 80 | 0 | 2 | 200 | 0.05 | 55 | 24248
66kV CB (Gas Insulated Busbars)(OD) (GM) | 30 | 100 | 100 | 80 | 0 | 2 | 100 | 0.05 | 55 | 12274
132kV CB (Air Insulated Busbars)(ID) (GM) | 80 | 100 | 100 | 80 | 0 | 1 | 400 | 0.05 | 55 | 128126
132kV CB (Air Insulated Busbars)(OD) (GM) | 80 | 100 | 100 | 80 | 0 | 1 | 100 | 0.05 | 55 | 32331
132kV CB (Gas Insulated Busbars)(ID) (GM) | 80 | 100 | 100 | 80 | 0 | 1 | 400 | 0.05 | 55 | 128126
132kV CB (Gas Insulated Busbars)(OD) (GM) | 80 | 100 | 100 | 80 | 0 | 1 | 100 | 0.05 | 55 | 32331
33kV Transformer (GM) | 30 | 100 | 100 | 80 | 0 | 2 | 400 | 0.05 | 55 | 48197
66kV Transformer | 30 | 100 | 100 | 80 | 0 | 2 | 400 | 0.05 | 55 | 48197
132kV Transformer | 80 | 100 | 100 | 80 | 0 | 1 | 800 | 0.05 | 55 | 255853